## TurenGonen
Conductor Tables - "Electric Power Distribution Engineering" (Turan Gonen) Second Edition. Appendix A. | [13 empty] | Same as DC | Same as 50 Hz | At 75% Capacity |  | Ta Resistance (Ω/Conductor/mi) | [7 empty] | Xa Inductive Reactance (Ω/Conductor/mi) at 1 ft Spacing |  |  | Xa' Shunt Capacitive Reactance (MΩ mi/Conductor) at 1 ft Spacing)
[18 empty] | 25C (77F) |  |  |  | 50C (122F) | [9 empty] | Hide | [5 empty] | Input for PowerFactory | [11 empty] | https://www.allaboutcircuits.com/textbook/direct-current/chpt-12/temperature-coefficient-resistance/
Type | Size of Conductor Circular Mils | AWG or B&S | Design Number | AL Strands | AL Layers | AL Strand Dia | ST Strands | ST Dia | Number of Strands | Diameter of Individual Strands (in) | Diameter (in) | Wall Thickness (in) | Outside Diameter (in) | Breaking Strength (lb) | Weight (Ib/mi) | Approx Current Carrying Capacity (amps) | Geometric Mean Radius at 60 Cycles (ft) | DC | 25 Cycles | 50 Cycles | 60 Cycles | DC2 | 25 Cycles3 | 50 Cycles4 | 60 Cycles5 | 25 Cycles6 | 50 Cycles7 | 60 Cycles8 | 25 Cycles9 | 50 Cycles10 | 60 Cycles11 | DC Resistance @ 25C (Ω/mi) | DC Resistance @ 20C (Ω/mi) | Outer Diameter (in) | GMR (ft) | Type Index | alpha | ID | Uniqueness | ID_ | GMR (mm) | Outer Diameter (mm) | MOT (C) | DC Resistance @ 20C (Ω/km) | Rating (kA) | DC Resistance @ MOT (Ω/km) | Type | MOT (C) | alpha | Material | alpha
CU- Hard Drawn | 1000000 | [7 empty] | 37 | 0.1644 |  |  | 1.151 | 43830 | 16300 | 1300 | 0.0368 | 0.0585 | 0.0594 | 0.062 | 0.0634 | 0.064 | 0.0648 | 0.0672 | 0.0685 | 0.1666 | 0.333 | 0.4 | 0.216 | 0.1081 | 0.0901 | 0.0585 | 0.057318 | 1.151 | 0.0368 | 6 | 0.004041 | 1000 kcmil CU- Hard Drawn (37) |  | 1000 kcmil CU- Hard Drawn (37) | 11.2166 | 29.2354 | 75 | 0.035616 | 1.3 | 0.043532 | ACSR | 95 | 0.004308 | Nickel | 0.005866
CU- Hard Drawn | 900000 | [7 empty] | 37 | 0.156 |  |  | 1.092 | 39610 | 14670 | 1220 | 0.0349 | 0.065 | 0.0658 | 0.0682 | 0.0695 | 0.0711 | 0.0718 | 0.074 | 0.0752 | 0.1693 | 0.339 | 0.406 | 0.22 | 0.11 | 0.0916 | 0.065 | 0.063687 | 1.092 | 0.0349 | 6 | 0.004041 | 900 kcmil CU- Hard Drawn (37) |  | 900 kcmil CU- Hard Drawn (37) | 10.6375 | 27.7368 | 75 | 0.039573 | 1.22 | 0.048368 | AL- Alcoa Hard Drawn | 90 | 0.004308 | Iron | 0.005671
CU- Hard Drawn | 800000 | [7 empty] | 37 | 0.147 |  |  | 1.029 | 35120 | 13040 | 1130 | 0.0329 | 0.0731 | 0.0739 | 0.076 | 0.0772 | 0.08 | 0.0808 | 0.0826 | 0.0837 | 0.1722 | 0.344 | 0.413 | 0.224 | 0.1121 | 0.0934 | 0.0731 | 0.071623 | 1.029 | 0.0329 | 6 | 0.004041 | 800 kcmil CU- Hard Drawn (37) |  | 800 kcmil CU- Hard Drawn (37) | 10.0279 | 26.1366 | 75 | 0.044504 | 1.13 | 0.054396 | AL- Alumoweld Strand OH Ground Wire | 90 | 0.004308 | Molybdenum | 0.004579
CU- Hard Drawn | 750000 | [7 empty] | 37 | 0.1424 |  |  | 0.997 | 33400 | 12230 | 1090 | 0.0319 | 0.078 | 0.0787 | 0.0807 | 0.06818 | 0.0853 | 0.0859 | 0.0878 | 0.0888 | 0.1739 | 0.348 | 0.417 | 0.225 | 0.1132 | 0.0943 | 0.078 | 0.076424 | 0.997 | 0.0319 | 6 | 0.004041 | 750 kcmil CU- Hard Drawn (37) |  | 750 kcmil CU- Hard Drawn (37) | 9.7231 | 25.3238 | 75 | 0.047488 | 1.09 | 0.058042 | CU- Anaconda Hollow | 75 | 0.004041 | Tungsten | 0.004403
CU- Hard Drawn | 700000 | [7 empty] | 37 | 0.1375 |  |  | 0.963 | 31170 | 11410 | 1040 | 0.0306 | 0.0836 | 0.0842 | 0.0661 | 0.0671 | 0.0914 | 0.092 | 0.0937 | 0.0947 | 0.1789 | 0.352 | 0.422 | 0.229 | 0.1145 | 0.0954 | 0.0836 | 0.081911 | 0.963 | 0.0306 | 6 | 0.004041 | 700 kcmil CU- Hard Drawn (37) |  | 700 kcmil CU- Hard Drawn (37) | 9.3269 | 24.4602 | 75 | 0.050897 | 1.04 | 0.062209 | CU- Copperweld | 75 | 0.004041 | Aluminum | 0.004308
CU- Hard Drawn | 500000 | [7 empty] | 37 | 0.1273 |  |  | 0.891 | 27020 | 9781 | 940 | 0.0285 | 0.0975 | 0.0981 | 0.0997 | 0.1006 | 0.1066 | 0.1071 | 0.1086 | 0.1095 | 0.1799 | 0.36 | 0.432 | 0.235 | 0.1173 | 0.0977 | 0.0975 | 0.09553 | 0.891 | 0.0285 | 6 | 0.004041 | 500 kcmil CU- Hard Drawn (37) | 1 | 500 kcmil CU- Hard Drawn (37) - 1 | 8.6868 | 22.6314 | 75 | 0.05936 | 0.94 | 0.072553 | CU- Hard Drawn | 75 | 0.004041 | Copper | 0.004041
CU- Hard Drawn | 500000 | [7 empty] | 37 | 0.1162 |  |  | 0.814 | 22610 | 8161 | 840 | 0.026 | 0.117 | 0.1175 | 0.1188 | 0.1196 | 0.128 | 0.1283 | 0.1296 | 0.1303 | 0.1845 | 0.369 | 0.443 | 0.241 | 0.1206 | 0.1004 | 0.117 | 0.11464 | 0.814 | 0.026 | 6 | 0.004041 | 500 kcmil CU- Hard Drawn (37) | 2 | 500 kcmil CU- Hard Drawn (37) - 2 | 7.9248 | 20.6756 | 75 | 0.071232 | 0.84 | 0.087063 | CU- HH Hollow | 75 | 0.004041 | Silver | 0.003819
CU- Hard Drawn | 500000 | [7 empty] | 19 | 0.1622 |  |  | 0.811 | 21590 | 8161 | 840 | 0.0256 | 0.117 | 0.1175 | 0.1188 | 0.1196 | 0.128 | 0.1283 | 0.1296 | 0.1303 | 0.1853 | 0.371 | 0.445 | 0.241 | 0.1206 | 0.1006 | 0.117 | 0.11464 | 0.811 | 0.0256 | 6 | 0.004041 | 500 kcmil CU- Hard Drawn (19) |  | 500 kcmil CU- Hard Drawn (19) | 7.8029 | 20.5994 | 75 | 0.071232 | 0.84 | 0.087063 |  |  |  | Platinum | 0.003729
CU- Hard Drawn | 450000 | [7 empty] | 19 | 0.1539 |  |  | 0.77 | 19750 | 7336 | 780 | 0.0243 | 0.13 | 0.1304 | 0.1316 | 0.1323 | 0.1422 | 0.1426 | 0.1437 | 0.1443 | 0.1879 | 0.376 | 0.451 | 0.245 | 0.1224 | 0.102 | 0.13 | 0.12737 | 0.77 | 0.0243 | 6 | 0.004041 | 450 kcmil CU- Hard Drawn (19) |  | 450 kcmil CU- Hard Drawn (19) | 7.4066 | 19.558 | 75 | 0.079146 | 0.78 | 0.096737 |  |  |  | Gold | 0.003715
CU- Hard Drawn | 400000 | [7 empty] | 19 | 0.1451 |  |  | 0.726 | 17560 | 6521 | 730 | 0.0229 | 0.1462 | 0.1466 | 0.1477 | 0.1484 | 0.16 | 0.1603 | 0.1613 | 0.1519 | 0.1909 | 0.382 | 0.458 | 0.249 | 0.1245 | 0.1038 | 0.1462 | 0.14325 | 0.726 | 0.0229 | 6 | 0.004041 | 400 kcmil CU- Hard Drawn (19) |  | 400 kcmil CU- Hard Drawn (19) | 6.9799 | 18.4404 | 75 | 0.089009 | 0.73 | 0.10879 |  |  |  | Zinc | 0.003847
CU- Hard Drawn | 350000 | [7 empty] | 19 | 0.1357 |  |  | 0.679 | 16890 | 5706 | 670 | 0.0214 | 0.1671 | 0.1675 | 0.1684 | 0.169 | 0.1828 | 0.1831 | 0.184 | 0.1845 | 0.1943 | 0.389 | 0.466 | 0.254 | 0.1269 | 0.1058 | 0.1671 | 0.16372 | 0.679 | 0.0214 | 6 | 0.004041 | 350 kcmil CU- Hard Drawn (19) |  | 350 kcmil CU- Hard Drawn (19) | 6.5227 | 17.2466 | 75 | 0.10173 | 0.67 | 0.12434 |  |  |  | Steel* | 0.003
CU- Hard Drawn | 350000 | [7 empty] | 12 | 0.1708 |  |  | 0.71 | 16140 | 5706 | 670 | 0.0225 | 0.1671 | 0.1675 | 0.1684 | 0.169 | 0.1828 | 0.1831 | 0.184 | 0.1845 | 0.1918 | 0.384 | 0.46 | 0.251 | 0.1253 | 0.1044 | 0.1671 | 0.16372 | 0.71 | 0.0225 | 6 | 0.004041 | 350 kcmil CU- Hard Drawn (12) |  | 350 kcmil CU- Hard Drawn (12) | 6.858 | 18.034 | 75 | 0.10173 | 0.67 | 0.12434 |  |  |  | Nichrome | 0.00017
CU- Hard Drawn | 300000 | [7 empty] | 19 | 0.1257 |  |  | 0.629 | 13510 | 4891 | 610 | 0.01987 | 0.195 | 0.1953 | 0.1961 | 0.1966 | 0.213 | 0.214 | 0.214 | 0.215 | 0.1982 | 0.396 | 0.476 | 0.259 | 0.1296 | 0.106 | 0.195 | 0.19106 | 0.629 | 0.01987 | 6 | 0.004041 | 300 kcmil CU- Hard Drawn (19) |  | 300 kcmil CU- Hard Drawn (19) | 6.0564 | 15.9766 | 75 | 0.11872 | 0.61 | 0.14511 |  |  |  | Nichrome V | 0.00013
CU- Hard Drawn | 300000 | [7 empty] | 12 | 0.1581 |  |  | 0.657 | 13170 | 4891 | 610 | 0.0208 | 0.195 | 0.1953 | 0.1961 | 0.1966 | 0.213 | 0.214 | 0.214 | 0.215 | 0.1957 | 0.392 | 0.47 | 0.256 | 0.1281 | 0.1068 | 0.195 | 0.19106 | 0.657 | 0.0208 | 6 | 0.004041 | 300 kcmil CU- Hard Drawn (12) |  | 300 kcmil CU- Hard Drawn (12) | 6.3398 | 16.6878 | 75 | 0.11872 | 0.61 | 0.14511 |  |  |  | Manganin | +/- 0.000015
CU- Hard Drawn | 250000 | [7 empty] | 19 | 0.1147 |  |  | 0.574 | 11360 | 4076 | 540 | 0.01813 | 0.234 | 0.234 | 0.235 | 0.236 | 0.256 | 0.256 | 0.257 | 0.257 | 0.203 | 0.406 | 0.487 | 0.266 | 0.1329 | 0.1108 | 0.234 | 0.22927 | 0.574 | 0.01813 | 6 | 0.004041 | 250 kcmil CU- Hard Drawn (19) |  | 250 kcmil CU- Hard Drawn (19) | 5.526 | 14.5796 | 75 | 0.14246 | 0.54 | 0.17413 |  |  |  | Constantan | -7.4e-05
CU- Hard Drawn | 250000 | [7 empty] | 12 | 0.1443 |  |  | 0.6 | 11130 | 4076 | 540 | 0.01902 | 0.234 | 0.234 | 0.235 | 0.236 | 0.256 | 0.256 | 0.257 | 0.257 | 0.2 | 0.401 | 0.481 | 0.263 | 0.1313 | 0.1094 | 0.234 | 0.22927 | 0.6 | 0.01902 | 6 | 0.004041 | 250 kcmil CU- Hard Drawn (12) |  | 250 kcmil CU- Hard Drawn (12) | 5.7973 | 15.24 | 75 | 0.14246 | 0.54 | 0.17413
CU- Hard Drawn | 211600 | 4/0 | [6 empty] | 19 | 0.1055 |  |  | 0.528 | 9617 | 3450 | 480 | 0.01668 | 0.276 | 0.277 | 0.277 | 0.278 | 0.302 | 0.303 | 0.303 | 0.303 | 0.207 | 0.414 | 0.497 | 0.272 | 0.1359 | 0.1132 | 0.276 | 0.27042 | 0.528 | 0.01668 | 6 | 0.004041 | 4/0 CU- Hard Drawn (19) |  | 4/0 CU- Hard Drawn (19) | 5.0841 | 13.4112 | 75 | 0.16803 | 0.48 | 0.20538
CU- Hard Drawn | 211600 | 4/0 | [6 empty] | 12 | 0.1328 |  |  | 0.552 | 9483 | 3450 | 490 | 0.0175 | 0.276 | 0.277 | 0.277 | 0.278 | 0.302 | 0.303 | 0.303 | 0.303 | 0.208 | 0.409 | 0.491 | 0.269 | 0.1343 | 0.1119 | 0.276 | 0.27042 | 0.552 | 0.0175 | 6 | 0.004041 | 4/0 CU- Hard Drawn (12) |  | 4/0 CU- Hard Drawn (12) | 5.334 | 14.0208 | 75 | 0.16803 | 0.49 | 0.20538
CU- Hard Drawn | 211600 | 4/0 | [6 empty] | 7 | 0.1739 |  |  | 0.522 | 9154 | 3450 | 480 | 0.01579 | 0.276 | 0.277 | 0.277 | 0.278 | 0.302 | 0.303 | 0.303 | 0.303 | 0.21 | 0.42 | 0.603 | 0.273 | 0.1363 | 0.1136 | 0.276 | 0.27042 | 0.522 | 0.01579 | 6 | 0.004041 | 4/0 CU- Hard Drawn (7) |  | 4/0 CU- Hard Drawn (7) | 4.8128 | 13.2588 | 75 | 0.16803 | 0.48 | 0.20538
CU- Hard Drawn | 167800 | 3/0 | [6 empty] | 12 | 0.1183 |  |  | 0.492 | 7556 | 2736 | 420 | 0.01569 | 0.349 | 0.349 | 0.349 | 0.35 | 0.381 | 0.381 | 0.382 | 0.382 | 0.21 | 0.421 | 0.606 | 0.277 | 0.1384 | 0.1153 | 0.349 | 0.34195 | 0.492 | 0.01569 | 6 | 0.004041 | 3/0 CU- Hard Drawn (12) |  | 3/0 CU- Hard Drawn (12) | 4.7823 | 12.4968 | 75 | 0.21248 | 0.42 | 0.2597
CU- Hard Drawn | 167800 | 3/0 | [6 empty] | 7 | 0.1548 |  |  | 0.464 | 7366 | 2736 | 420 | 0.01404 | 0.349 | 0.349 | 0.349 | 0.35 | 0.381 | 0.381 | 0.382 | 0.382 | 0.216 | 0.431 | 0.518 | 0.281 | 0.1405 | 0.1171 | 0.349 | 0.34195 | 0.464 | 0.01404 | 6 | 0.004041 | 3/0 CU- Hard Drawn (7) |  | 3/0 CU- Hard Drawn (7) | 4.2794 | 11.7856 | 75 | 0.21248 | 0.42 | 0.2597
CU- Hard Drawn | 133100 | 2/0 | [6 empty] | 7 | 0.1379 |  |  | 0.414 | 5926 | 2170 | 360 | 0.01252 | 0.44 | 0.44 | 0.44 | 0.44 | 0.481 | 0.481 | 0.481 | 0.481 | 0.222 | 0.443 | 0.532 | 0.289 | 0.1445 | 0.1205 | 0.44 | 0.43111 | 0.414 | 0.01252 | 6 | 0.004041 | 2/0 CU- Hard Drawn (7) |  | 2/0 CU- Hard Drawn (7) | 3.8161 | 10.5156 | 75 | 0.26788 | 0.36 | 0.32742
CU- Hard Drawn | 106600 | 1/0 | [6 empty] | 7 | 0.1228 |  |  | 0.368 | 4752 | 1720 | 310 | 0.01113 | 0.555 | 0.555 | 0.555 | 0.555 | 0.606 | 0.607 | 0.607 | 0.607 | 0.227 | 0.455 | 0.546 | 0.298 | 0.1488 | 0.124 | 0.555 | 0.54379 | 0.368 | 0.01113 | 6 | 0.004041 | 1/0 CU- Hard Drawn (7) |  | 1/0 CU- Hard Drawn (7) | 3.3924 | 9.3472 | 75 | 0.33789 | 0.31 | 0.41299
CU- Hard Drawn | 83690 | 1 | [6 empty] | 7 | 0.1093 |  |  | 0.328 | 3804 | 1364 | 270 | 0.00992 | 0.599 | 0.699 | 0.699 | 0.699 | 0.766 | 0.766 | 0.766 | 0.766 | 0.233 | 0.467 | 0.56 | 0.306 | 0.1528 | 0.1274 | 0.599 | 0.5869 | 0.328 | 0.00992 | 6 | 0.004041 | 1 CU- Hard Drawn (7) |  | 1 CU- Hard Drawn (7) | 3.0236 | 8.3312 | 75 | 0.36468 | 0.27 | 0.44573
CU- Hard Drawn | 63690 | 1 | [6 empty] | 3 | 0.167 |  |  | 0.36 | 3620 | 1351 | 270 | 0.01016 | 0.692 | 0.692 | 0.692 | 0.692 | 0.757 | 0.757 | 0.757 | 0.757 | 0.232 | 0.464 | 0.557 | 0.299 | 0.1495 | 0.1246 | 0.692 | 0.67802 | 0.36 | 0.01016 | 6 | 0.004041 | 1 CU- Hard Drawn (3) |  | 1 CU- Hard Drawn (3) | 3.0968 | 9.144 | 75 | 0.4213 | 0.27 | 0.51494
CU- Hard Drawn | 66370 | 2 | [6 empty] | 7 | 0.0974 |  |  | 0.292 | 3045 | 1082 | 230 | 0.00883 | 0.881 | 0.882 | 0.882 | 0.882 | 0.964 | 0.964 | 0.964 | 0.964 | 0.239 | 0.478 | 0.574 | 0.314 | 0.157 | 0.1308 | 0.881 | 0.8632 | 0.292 | 0.00883 | 6 | 0.004041 | 2 CU- Hard Drawn (7) |  | 2 CU- Hard Drawn (7) | 2.6914 | 7.4168 | 75 | 0.53637 | 0.23 | 0.65558
CU- Hard Drawn | 66370 | 2 | [6 empty] | 3 | 0.1487 |  |  | 0.32 | 2913 | 1071 | 240 | 0.00903 | 0.873 | 0.873 | 0.873 | 0.873 | 0.956 | 0.956 | 0.956 | 0.956 | 0.238 | 0.476 | 0.571 | 0.307 | 0.1637 | 0.1281 | 0.873 | 0.85536 | 0.32 | 0.00903 | 6 | 0.004041 | 2 CU- Hard Drawn (3) |  | 2 CU- Hard Drawn (3) | 2.7523 | 8.128 | 75 | 0.5315 | 0.24 | 0.64962
CU- Hard Drawn | 66370 | 2 | [6 empty] | 1 |  |  |  | 0.258 | 3003 | 1061 | 220 | 0.00836 | 0.884 | 0.884 | 0.884 | 0.884 | 0.946 | 0.946 | 0.946 | 0.946 | 0.242 | 0.484 | 0.581 | 0.323 | 0.1614 | 0.1346 | 0.884 | 0.86614 | 0.258 | 0.00836 | 6 | 0.004041 | 2 CU- Hard Drawn (1) |  | 2 CU- Hard Drawn (1) | 2.5481 | 6.5532 | 75 | 0.53819 | 0.22 | 0.65781
CU- Hard Drawn | 52630 | 3 | [6 empty] | 7 | 0.0867 |  |  | 0.26 | 2433 | 858 | 200 | 0.00787 | 1.112 | 1.112 | 1.112 | 1.112 | 1.216 | 1.216 | 1.216 | 1.216 | 0.245 | 0.49 | 0.588 | 0.322 | 0.1611 | 0.1343 | 1.112 | 1.0895 | 0.26 | 0.00787 | 6 | 0.004041 | 3 CU- Hard Drawn (7) |  | 3 CU- Hard Drawn (7) | 2.3988 | 6.604 | 75 | 0.677 | 0.2 | 0.82747
CU- Hard Drawn | 52630 | 3 | [6 empty] | 3 | 0.1325 |  |  | 0.286 | 2359 | 850 | 200 | 0.00805 | 1.101 | 1.101 | 1.101 | 1.101 | 1.204 | 1.204 | 1.204 | 1.204 | 0.244 | 0.488 | 0.585 | 0.316 | 0.1578 | 0.1315 | 1.101 | 1.0788 | 0.286 | 0.00805 | 6 | 0.004041 | 3 CU- Hard Drawn (3) |  | 3 CU- Hard Drawn (3) | 2.4536 | 7.2644 | 75 | 0.67031 | 0.2 | 0.81929
CU- Hard Drawn | 52630 | 3 | [6 empty] | 1 |  |  |  | 0.229 | 2439 | 841 | 190 | 0.00745 | 1.09 | 1.09 | 1.09 | 1.09 | 1.192 | 1.192 | 1.192 | 1.192 | 0.248 | 0.496 | 0.595 | 0.331 | 0.1656 | 0.138 | 1.09 | 1.068 | 0.229 | 0.00745 | 6 | 0.004041 | 3 CU- Hard Drawn (1) |  | 3 CU- Hard Drawn (1) | 2.2708 | 5.8166 | 75 | 0.66361 | 0.19 | 0.8111
CU- Hard Drawn | 41740 | 4 | [6 empty] | 3 | 0.118 |  |  | 0.254 | 1879 | 674 | 180 | 0.00717 | 1.388 | 1.388 | 1.388 | 1.388 | 1.518 | 1.518 | 1.518 | 1.518 | 0.25 | 0.499 | 0.599 | 0.324 | 0.1619 | 0.1349 | 1.388 | 1.36 | 0.254 | 0.00717 | 6 | 0.004041 | 4 CU- Hard Drawn (3) |  | 4 CU- Hard Drawn (3) | 2.1854 | 6.4516 | 75 | 0.84504 | 0.18 | 1.0329
CU- Hard Drawn | 41740 | 4 | [6 empty] | 1 |  |  |  | 0.204 | 1970 | 667 | 170 | 0.00663 | 1.374 | 1.374 | 1.374 | 1.374 | 1.503 | 1.503 | 1.503 | 1.503 | 0.264 | 0.507 | 0.609 | 0.339 | 0.1697 | 0.1416 | 1.374 | 1.3462 | 0.204 | 0.00663 | 6 | 0.004041 | 4 CU- Hard Drawn (1) |  | 4 CU- Hard Drawn (1) | 2.0208 | 5.1816 | 75 | 0.83651 | 0.17 | 1.0224
CU- Hard Drawn | 33100 | 5 | [6 empty] | 3 | 0.105 |  |  | 0.226 | 1605 | 534 | 180 | 0.00638 | 1.75 | 1.75 | 1.75 | 1.75 | 1.914 | 1.914 | 1.914 | 1.914 | 0.256 | 0.511 | 0.613 | 0.332 | 0.1661 | 0.1384 | 1.75 | 1.7146 | 0.226 | 0.00638 | 6 | 0.004041 | 5 CU- Hard Drawn (3) |  | 5 CU- Hard Drawn (3) | 1.9446 | 5.7404 | 75 | 1.0654 | 0.18 | 1.3022
CU- Hard Drawn | 33100 | 5 | [6 empty] | 1 |  |  |  | 0.1819 | 1591 | 529 | 140 | 0.0059 | 1.733 | 1.733 | 1.733 | 1.733 | 1.895 | 1.895 | 1.895 | 1.895 | 0.26 | 0.519 | 0.623 | 0.348 | 0.1738 | 0.1449 | 1.733 | 1.698 | 0.1819 | 0.0059 | 6 | 0.004041 | 5 CU- Hard Drawn (1) |  | 5 CU- Hard Drawn (1) | 1.7983 | 4.6203 | 75 | 1.0551 | 0.14 | 1.2896
CU- Hard Drawn | 26250 | 6 | [6 empty] | 3 | 0.0935 |  |  | 0.201 | 1205 | 424 | 130 | 0.00568 | 2.21 | 2.21 | 2.21 | 2.21 | 2.41 | 2.41 | 2.41 | 2.41 | 0.262 | 0.523 | 0.628 | 0.341 | 0.1703 | 0.1419 | 2.21 | 2.1653 | 0.201 | 0.00568 | 6 | 0.004041 | 6 CU- Hard Drawn (3) |  | 6 CU- Hard Drawn (3) | 1.7313 | 5.1054 | 75 | 1.3455 | 0.13 | 1.6445
CU- Hard Drawn | 26250 | 6 | [6 empty] | 1 |  |  |  | 0.162 | 1280 | 420 | 120 | 0.00526 | 2.18 | 2.18 | 2.18 | 2.18 | 2.39 | 2.39 | 2.39 | 2.39 | 0.265 | 0.531 | 0.637 | 0.356 | 0.1779 | 0.1483 | 2.18 | 2.136 | 0.162 | 0.00526 | 6 | 0.004041 | 6 CU- Hard Drawn (1) |  | 6 CU- Hard Drawn (1) | 1.6032 | 4.1148 | 75 | 1.3272 | 0.12 | 1.6222
CU- Hard Drawn | 20820 | 7 | [6 empty] | 1 |  |  |  | 0.1443 | 1030 | 333 | 110 | 0.00468 | 2.75 | 2.75 | 2.75 | 2.75 | 3.01 | 3.01 | 3.01 | 3.01 | 0.271 | 0.542 | 0.651 | 0.364 | 0.1821 | 0.1517 | 2.75 | 2.6944 | 0.1443 | 0.00468 | 6 | 0.004041 | 7 CU- Hard Drawn (1) |  | 7 CU- Hard Drawn (1) | 1.4265 | 3.6652 | 75 | 1.6742 | 0.11 | 2.0464
CU- Hard Drawn | 16510 | 8 | [6 empty] | 1 |  |  |  | 0.1286 | 826 | 264 | 90 | 0.00417 | 3.47 | 3.47 | 3.47 | 3.47 | 3.8 | 3.8 | 3.8 | 3.8 | 0.277 | 0.564 | 0.665 | 0.372 | 0.1862 | 0.1652 | 3.47 | 3.3999 | 0.1286 | 0.00417 | 6 | 0.004041 | 8 CU- Hard Drawn (1) |  | 8 CU- Hard Drawn (1) | 1.271 | 3.2664 | 75 | 2.1126 | 0.09 | 2.5821
CU- Anaconda Hollow | 890500 |  | 966 | [5 empty] | 28 |  | 0.161 |  | 1.65 | 36000 | 15085 | 1395 | 0.0612 | 0.0671 | 0.0671 | 0.0676 | 0.0676 | 0.0734 | 0.0734 | 0.0739 | 0.0739 | 0.1412 | 0.282 | 0.339 | 0.1907 | 0.0953 | 0.0794 | 0.0671 | 0.065744 | 1.65 | 0.0612 | 4 | 0.004041 | 966 CU- Anaconda Hollow (28) |  | 966 CU- Anaconda Hollow (28) | 18.6538 | 41.91 | 75 | 0.040852 | 1.395 | 0.049931
CU- Anaconda Hollow | 750000 |  | 96R 1 | [5 empty] | 42 |  | 0.1296 |  | 1.155 | 34200 | 12345 | 1160 | 0.0408 | 0.0786 | 0.0786 | 0.0791 | 0.0791 | 0.086 | 0.086 | 0.0865 | 0.0865 | 0.1617 | 0.323 | 0.388 | 0.216 | 0.108 | 0.09 | 0.0786 | 0.077012 | 1.155 | 0.0408 | 4 | 0.004041 | 96R 1 CU- Anaconda Hollow (42) |  | 96R 1 CU- Anaconda Hollow (42) | 12.4358 | 29.337 | 75 | 0.047853 | 1.16 | 0.058489
CU- Anaconda Hollow | 650000 |  | 939 | [5 empty] | 50 |  | 0.1097 |  | 1.126 | 29500 | 10761 | 1060 | 0.0406 | 0.0909 | 0.0909 | 0.0915 | 0.0915 | 0.0994 | 0.0994 | 0.1001 | 0.1001 | 0.1621 | 0.324 | 0.389 | 0.218 | 0.1089 | 0.0908 | 0.0909 | 0.089063 | 1.126 | 0.0406 | 4 | 0.004041 | 939 CU- Anaconda Hollow (50) |  | 939 CU- Anaconda Hollow (50) | 12.3749 | 28.6004 | 75 | 0.055341 | 1.06 | 0.067641
CU- Anaconda Hollow | 600000 |  | 360R 1 | [5 empty] | 50 |  | 0.1053 |  | 1.007 | 27500 | 9905 | 1020 | 0.0387 | 0.0984 | 0.0984 | 0.0991 | 0.0991 | 0.1077 | 0.1077 | 0.1084 | 0.1084 | 0.1644 | 0.329 | 0.395 | 0.221 | 0.1105 | 0.0921 | 0.0984 | 0.096412 | 1.007 | 0.0387 | 4 | 0.004041 | 360R 1 CU- Anaconda Hollow (50) |  | 360R 1 CU- Anaconda Hollow (50) | 11.7958 | 25.5778 | 75 | 0.059908 | 1.02 | 0.073222
CU- Anaconda Hollow | 550000 |  | 938 | [5 empty] | 50 |  | 0.1009 |  | 1.036 | 25200 | 9103 | 960 | 0.0373 | 0.1076 | 0.1076 | 0.1081 | 0.1081 | 0.1177 | 0.1177 | 0.1183 | 0.1183 | 0.1663 | 0.333 | 0.399 | 0.224 | 0.1119 | 0.0932 | 0.1076 | 0.10543 | 1.036 | 0.0373 | 4 | 0.004041 | 938 CU- Anaconda Hollow (50) |  | 938 CU- Anaconda Hollow (50) | 11.369 | 26.3144 | 75 | 0.065509 | 0.96 | 0.080068
CU- Anaconda Hollow | 510000 |  | 4R5 | [5 empty] | 50 |  | 0.097 |  | 1 | 22700 | 8485 | 910 | 0.036 | 0.173 | 0.173 | 0.1178 | 0.1178 | 0.1283 | 0.1283 | 0.1289 | 0.1289 | 0.1681 | 0.336 | 0.404 | 0.226 | 0.1131 | 0.0943 | 0.173 | 0.1695 | 1 | 0.036 | 4 | 0.004041 | 4R5 CU- Anaconda Hollow (50) |  | 4R5 CU- Anaconda Hollow (50) | 10.9728 | 25.4 | 75 | 0.10533 | 0.91 | 0.12873
CU- Anaconda Hollow | 500000 |  | 892R3 | [5 empty] | 18 |  | 0.1558 |  | 1.08 | 21400 | 8263 | 900 | 0.0394 | 0.1178 | 0.1178 | 0.1184 | 0.1184 | 0.1289 | 0.1289 | 0.1296 | 0.1296 | 0.163 | 0.326 | 0.391 | 0.221 | 0.1164 | 0.092 | 0.1178 | 0.11542 | 1.08 | 0.0394 | 4 | 0.004041 | 892R3 CU- Anaconda Hollow (18) |  | 892R3 CU- Anaconda Hollow (18) | 12.0091 | 27.432 | 75 | 0.071719 | 0.9 | 0.087658
CU- Anaconda Hollow | 450000 |  | 933 | [5 empty] | 21 |  | 0.1353 |  | 1.074 | 19300 | 7476 | 850 | 0.0398 | 0.1319 | 0.1319 | 0.1324 | 0.1324 | 0.1443 | 0.1443 | 0.1448 | 0.1448 | 0.163 | 0.326 | 0.391 | 0.221 | 0.1106 | 0.0922 | 0.1319 | 0.12923 | 1.074 | 0.0398 | 4 | 0.004041 | 933 CU- Anaconda Hollow (21) |  | 933 CU- Anaconda Hollow (21) | 12.131 | 27.2796 | 75 | 0.080303 | 0.85 | 0.098151
CU- Anaconda Hollow | 400000 |  | 924 | [5 empty] | 21 |  | 0.1227 |  | 1.014 | 17200 | 6642 | 810 | 0.0376 | 0.1485 | 0.1485 | 0.1491 | 0.1491 | 0.1624 | 0.1624 | 0.1631 | 0.1631 | 0.1658 | 0.332 | 0.398 | 0.225 | 0.1126 | 0.0939 | 0.1485 | 0.1455 | 1.014 | 0.0376 | 4 | 0.004041 | 924 CU- Anaconda Hollow (21) |  | 924 CU- Anaconda Hollow (21) | 11.4605 | 25.7556 | 75 | 0.090409 | 0.81 | 0.1105
CU- Anaconda Hollow | 380500 |  | 925R 1 | [5 empty] | 22 |  | 0.1211 |  | 1.003 | 16300 | 6331 | 780 | 0.0373 | 0.1565 | 0.1565 | 0.1572 | 0.1572 | 0.1712 | 0.1712 | 0.1719 | 0.1719 | 0.1663 | 0.333 | 0.399 | 0.226 | 0.113 | 0.0942 | 0.1565 | 0.15334 | 1.003 | 0.0373 | 4 | 0.004041 | 925R 1 CU- Anaconda Hollow (22) |  | 925R 1 CU- Anaconda Hollow (22) | 11.369 | 25.4762 | 75 | 0.09528 | 0.78 | 0.11646
CU- Anaconda Hollow | 350000 |  | 565R 1 | [5 empty] | 21 |  | 0.1196 |  | 0.95 | 15100 | 5813 | 750 | 0.0353 | 0.1695 | 0.1695 | 0.17 | 0.17 | 0.1854 | 0.1854 | 0.186 | 0.186 | 0.1691 | 0.338 | 0.406 | 0.23 | 0.115 | 0.0958 | 0.1695 | 0.16608 | 0.95 | 0.0353 | 4 | 0.004041 | 565R 1 CU- Anaconda Hollow (21) |  | 565R 1 CU- Anaconda Hollow (21) | 10.7594 | 24.13 | 75 | 0.10319 | 0.75 | 0.12613
CU- Anaconda Hollow | 350000 |  | 936 | [5 empty] | 15 |  | 0.1444 |  | 0.86 | 15400 | 5776 | 740 | 0.0311 | 0.169 | 0.169 | 0.1695 | 0.1695 | 0.1849 | 0.1849 | 0.1854 | 0.1854 | 0.1754 | 0.351 | 0.421 | 0.237 | 0.1185 | 0.0988 | 0.169 | 0.16559 | 0.86 | 0.0311 | 4 | 0.004041 | 936 CU- Anaconda Hollow (15) |  | 936 CU- Anaconda Hollow (15) | 9.4793 | 21.844 | 75 | 0.10289 | 0.74 | 0.12576
CU- Anaconda Hollow | 350000 |  | 378R 1 | [5 empty] | 30 |  | 0.1059 |  | 0.736 | 16100 | 5739 | 700 | 0.0253 | 0.1685 | 0.1685 | 0.169 | 0.169 | 0.1843 | 0.1843 | 0.1849 | 0.1849 | 0.186 | 0.372 | 0.446 | 0.248 | 0.1241 | 0.1034 | 0.1685 | 0.1651 | 0.736 | 0.0253 | 4 | 0.004041 | 378R 1 CU- Anaconda Hollow (30) |  | 378R 1 CU- Anaconda Hollow (30) | 7.7114 | 18.6944 | 75 | 0.10259 | 0.7 | 0.12539
CU- Anaconda Hollow | 321000 |  | 954 | [5 empty] | 22 |  | 0.1113 |  | 0.92 | 13850 | 5343 | 700 | 0.034 | 0.1851 | 0.1851 | 0.1856 | 0.1856 | 0.202 | 0.202 | 0.203 | 0.203 | 0.171 | 0.342 | 0.41 | 0.232 | 0.1161 | 0.0968 | 0.1851 | 0.18136 | 0.92 | 0.034 | 4 | 0.004041 | 954 CU- Anaconda Hollow (22) |  | 954 CU- Anaconda Hollow (22) | 10.3632 | 23.368 | 75 | 0.11269 | 0.7 | 0.13774
CU- Anaconda Hollow | 300000 |  | 935 | [5 empty] | 18 |  | 0.1205 |  | 0.839 | 13100 | 4984 | 670 | 0.0307 | 0.198 | 0.198 | 0.1985 | 0.1985 | 0.216 | 0.216 | 0.217 | 0.217 | 0.1761 | 0.352 | 0.423 | 0.239 | 0.1194 | 0.0995 | 0.198 | 0.194 | 0.839 | 0.0307 | 4 | 0.004041 | 935 CU- Anaconda Hollow (18) |  | 935 CU- Anaconda Hollow (18) | 9.3574 | 21.3106 | 75 | 0.12055 | 0.67 | 0.14734
CU- Anaconda Hollow | 300000 |  | 903R 1 | [5 empty] | 15 |  | 0.1338 |  | 0.797 | 13200 | 4953 | 660 | 0.0289 | 0.1969 | 0.1969 | 0.1975 | 0.1975 | 0.215 | 0.215 | 0.216 | 0.216 | 0.1793 | 0.359 | 0.43 | 0.242 | 0.1212 | 0.101 | 0.1969 | 0.19292 | 0.797 | 0.0289 | 4 | 0.004041 | 903R 1 CU- Anaconda Hollow (15) |  | 903R 1 CU- Anaconda Hollow (15) | 8.8087 | 20.2438 | 75 | 0.11988 | 0.66 | 0.14652
CU- Anaconda Hollow | 300000 |  | 178R2 | [5 empty] | 12 |  | 0.1507 |  | 0.75 | 13050 | 4937 | 650 | 0.0266 | 0.1964 | 0.1964 | 0.1969 | 0.1969 | 0.215 | 0.215 | 0.216 | 0.216 | 0.1833 | 0.367 | 0.44 | 0.247 | 0.1234 | 0.1028 | 0.1964 | 0.19243 | 0.75 | 0.0266 | 4 | 0.004041 | 178R2 CU- Anaconda Hollow (12) |  | 178R2 CU- Anaconda Hollow (12) | 8.1077 | 19.05 | 75 | 0.11957 | 0.65 | 0.14615
CU- Anaconda Hollow | 250000 |  | 926 | [5 empty] | 18 |  | 0.11 |  | 0.766 | 10950 | 4155 | 600 | 0.0279 | 0.238 | 0.238 | 0.239 | 0.239 | 0.26 | 0.26 | 0.261 | 0.261 | 0.181 | 0.362 | 0.434 | 0.245 | 0.1226 | 0.1022 | 0.238 | 0.23319 | 0.766 | 0.0279 | 4 | 0.004041 | 926 CU- Anaconda Hollow (18) |  | 926 CU- Anaconda Hollow (18) | 8.5039 | 19.4564 | 75 | 0.1449 | 0.6 | 0.1771
CU- Anaconda Hollow | 250000 |  | 915R 1 | [5 empty] | 15 |  | 0.1214 |  | 0.725 | 11000 | 4148 | 590 | 0.0266 | 0.237 | 0.237 | 0.238 | 0.238 | 0.259 | 0.259 | 0.26 | 0.26 | 0.1834 | 0.367 | 0.44 | 0.249 | 0.1246 | 0.1038 | 0.237 | 0.23221 | 0.725 | 0.0266 | 4 | 0.004041 | 915R 1 CU- Anaconda Hollow (15) |  | 915R 1 CU- Anaconda Hollow (15) | 8.1077 | 18.415 | 75 | 0.14429 | 0.59 | 0.17636
CU- Anaconda Hollow | 250000 |  | 24R 1 | [5 empty] | 12 |  | 0.1368 |  | 0.683 | 11000 | 4133 | 580 | 0.0245 | 0.237 | 0.237 | 0.238 | 0.238 | 0.259 | 0.259 | 0.26 | 0.26 | 0.1876 | 0.375 | 0.45 | 0.253 | 0.1267 | 0.1066 | 0.237 | 0.23221 | 0.683 | 0.0245 | 4 | 0.004041 | 24R 1 CU- Anaconda Hollow (12) |  | 24R 1 CU- Anaconda Hollow (12) | 7.4676 | 17.3482 | 75 | 0.14429 | 0.58 | 0.17636
CU- Anaconda Hollow | 4/0 | 4/0 | 923 | [5 empty] | 18 |  | 0.1005 |  | 0.7 | 9300 | 3521 | 530 | 0.0255 | 0.281 | 0.281 | 0.282 | 0.282 | 0.307 | 0.307 | 0.308 | 0.308 | 0.1855 | 0.371 | 0.445 | 0.252 | 0.1258 | 0.1049 | 0.281 | 0.27532 | 0.7 | 0.0255 | 4 | 0.004041 | 4/0 CU- Anaconda Hollow (18) |  | 4/0 CU- Anaconda Hollow (18) | 7.7724 | 17.78 | 75 | 0.17108 | 0.53 | 0.2091
CU- Anaconda Hollow | 4/0 | 4/0 | 922 | [5 empty] | 15 |  | 0.1109 |  | 0.663 | 9300 | 3510 | 520 | 0.0238 | 0.281 | 0.281 | 0.282 | 0.282 | 0.307 | 0.307 | 0.308 | 0.308 | 0.1889 | 0.378 | 0.453 | 0.256 | 0.1278 | 0.1065 | 0.281 | 0.27532 | 0.663 | 0.0238 | 4 | 0.004041 | 4/0 CU- Anaconda Hollow (15) |  | 4/0 CU- Anaconda Hollow (15) | 7.2542 | 16.8402 | 75 | 0.17108 | 0.52 | 0.2091
CU- Anaconda Hollow | 4/0 | 4/0 | 50R2 | [5 empty] | 14 |  | 0.1152 |  | 0.65 | 9300 | 3510 | 520 | 0.0234 | 0.28 | 0.28 | 0.281 | 0.281 | 0.306 | 0.306 | 0.307 | 0.307 | 0.1898 | 0.38 | 0.455 | 0.257 | 0.1285 | 0.1071 | 0.28 | 0.27434 | 0.65 | 0.0234 | 4 | 0.004041 | 4/0 CU- Anaconda Hollow (14) |  | 4/0 CU- Anaconda Hollow (14) | 7.1323 | 16.51 | 75 | 0.17047 | 0.52 | 0.20836
CU- Anaconda Hollow | 3/0 | 3/0 | 158R 1 | [5 empty] | 16 |  | 0.0961 |  | 0.606 | 7500 | 2785 | 460 | 0.0221 | 0.354 | 0.354 | 0.355 | 0.355 | 0.387 | 0.387 | 0.388 | 0.388 | 0.1928 | 0.386 | 0.463 | 0.262 | 0.131 | 0.1091 | 0.354 | 0.34685 | 0.606 | 0.0221 | 4 | 0.004041 | 3/0 CU- Anaconda Hollow (16) |  | 3/0 CU- Anaconda Hollow (16) | 6.7361 | 15.3924 | 75 | 0.21552 | 0.46 | 0.26342
CU- Anaconda Hollow | 3/0 | 3/0 | 495R 1 | [5 empty] | 15 |  | 0.0996 |  | 0.595 | 7600 | 2785 | 460 | 0.0214 | 0.353 | 0.353 | 0.354 | 0.354 | 0.386 | 0.386 | 0.387 | 0.387 | 0.1943 | 0.389 | 0.466 | 0.263 | 0.1316 | 0.1097 | 0.353 | 0.34587 | 0.595 | 0.0214 | 4 | 0.004041 | 3/0 CU- Anaconda Hollow (15) |  | 3/0 CU- Anaconda Hollow (15) | 6.5227 | 15.113 | 75 | 0.21491 | 0.46 | 0.26268
CU- Anaconda Hollow | 3/0 | 3/0 | 570R 2 | [5 empty] | 12 |  | 0.1123 |  | 0.56 | 7600 | 2772 | 450 | 0.0201 | 0.352 | 0.352 | 0.353 | 0.353 | 0.385 | 0.385 | 0.386 | 0.386 | 0.1976 | 0.395 | 0.474 | 0.268 | 0.1338 | 0.1115 | 0.352 | 0.34489 | 0.56 | 0.0201 | 4 | 0.004041 | 3/0 CU- Anaconda Hollow (12) |  | 3/0 CU- Anaconda Hollow (12) | 6.1265 | 14.224 | 75 | 0.2143 | 0.45 | 0.26193
CU- Anaconda Hollow | 2/0 | 2/0 | 909R 2 | [5 empty] | 15 |  | 0.088 |  | 0.53 | 5950 | 2213 | 370 | 0.0191 | 0.446 | 0.446 | 0.446 | 0.446 | 0.487 | 0.487 | 0.487 | 0.487 | 0.2 | 0.4 | 0.481 | 0.271 | 0.1357 | 0.1131 | 0.446 | 0.43699 | 0.53 | 0.0191 | 4 | 0.004041 | 2/0 CU- Anaconda Hollow (15) |  | 2/0 CU- Anaconda Hollow (15) | 5.8217 | 13.462 | 75 | 0.27153 | 0.37 | 0.33188
CU- Anaconda Hollow | 2/0 | 2/0 | 412R2 | [5 empty] | 14 |  | 0.0913 |  | 0.515 | 6000 | 2207 | 370 | 0.0184 | 0.446 | 0.446 | 0.446 | 0.446 | 0.487 | 0.487 | 0.487 | 0.487 | 0.202 | 0.404 | 0.485 | 0.274 | 0.1368 | 0.114 | 0.446 | 0.43699 | 0.515 | 0.0184 | 4 | 0.004041 | 2/0 CU- Anaconda Hollow (14) |  | 2/0 CU- Anaconda Hollow (14) | 5.6083 | 13.081 | 75 | 0.27153 | 0.37 | 0.33188
CU- Anaconda Hollow | 2/0 | 2/0 | 937 | [5 empty] | 13 |  | 0.095 |  | 0.505 | 6000 | 2203 | 370 | 0.0181 | 0.446 | 0.446 | 0.446 | 0.446 | 0.487 | 0.487 | 0.487 | 0.487 | 0.203 | 0.406 | 0.487 | 0.275 | 0.1375 | 0.1146 | 0.446 | 0.43699 | 0.505 | 0.0181 | 4 | 0.004041 | 2/0 CU- Anaconda Hollow (13) |  | 2/0 CU- Anaconda Hollow (13) | 5.5169 | 12.827 | 75 | 0.27153 | 0.37 | 0.33188
CU- Anaconda Hollow | 125600 |  | 930 | [5 empty] | 14 |  | 0.0885 |  | 0.5 | 5650 | 2083 | 360 | 0.018 | 0.473 | 0.473 | 0.473 | 0.473 | 0.517 | 0.517 | 0.517 | 0.517 | 0.203 | 0.406 | 0.487 | 0.276 | 0.1378 | 0.1149 | 0.473 | 0.46344 | 0.5 | 0.018 | 4 | 0.004041 | 930 CU- Anaconda Hollow (14) |  | 930 CU- Anaconda Hollow (14) | 5.4864 | 12.7 | 75 | 0.28797 | 0.36 | 0.35197
CU- Anaconda Hollow | 121300 |  | 934 | [5 empty] | 15 |  | 0.0836 |  | 0.5 | 5400 | 2015 | 350 | 0.0179 | 0.491 | 0.491 | 0.491 | 0.491 | 0.537 | 0.537 | 0.537 | 0.537 | 0.203 | 0.407 | 0.488 | 0.276 | 0.1378 | 0.1149 | 0.491 | 0.48108 | 0.5 | 0.0179 | 4 | 0.004041 | 934 CU- Anaconda Hollow (15) |  | 934 CU- Anaconda Hollow (15) | 5.4559 | 12.7 | 75 | 0.29893 | 0.35 | 0.36537
CU- Anaconda Hollow | 119400 |  | 901 | [5 empty] | 12 |  | 0.0936 |  | 0.47 | 5300 | 1979 | 340 | 0.0165 | 0.507 | 0.507 | 0.507 | 0.507 | 0.555 | 0.555 | 0.555 | 0.555 | 0.207 | 0.415 | 0.498 | 0.28 | 0.14 | 0.1167 | 0.507 | 0.49676 | 0.47 | 0.0165 | 4 | 0.004041 | 901 CU- Anaconda Hollow (12) |  | 901 CU- Anaconda Hollow (12) | 5.0292 | 11.938 | 75 | 0.30867 | 0.34 | 0.37727
CU- HH Hollow | 1000000 | [10 empty] | 0.15 | 2.103 | 43190 | 16160 | 1620 | 0.0833 | 0.0576 | 0.0576 | 0.0577 | 0.0577 | 0.063 | 0.063 | 0.0631 | 0.0631 | 0.1257 | 0.251 | 0.302 | 0.1734 | 0.0867 | 0.0722 | 0.0576 | 0.056436 | 2.103 | 0.0833 | 7 | 0.004041 | 1000 kcmil CU- HH Hollow |  | 1000 kcmil CU- HH Hollow | 25.3898 | 53.4162 | 75 | 0.035068 | 1.62 | 0.042862
CU- HH Hollow | 950000 | [10 empty] | 0.147 | 2.035 | 41030 | 15350 | 1565 | 0.0805 | 0.0606 | 0.0606 | 0.0607 | 0.0607 | 0.0663 | 0.0664 | 0.0664 | 0.0664 | 0.1274 | 0.255 | 0.306 | 0.1757 | 0.0879 | 0.0732 | 0.0606 | 0.059376 | 2.035 | 0.0805 | 7 | 0.004041 | 950 kcmil CU- HH Hollow |  | 950 kcmil CU- HH Hollow | 24.5364 | 51.689 | 75 | 0.036894 | 1.565 | 0.045094
CU- HH Hollow | 900000 | [10 empty] | 0.144 | 1.966 | 38870 | 14540 | 1505 | 0.0778 | 0.064 | 0.064 | 0.0641 | 0.0641 | 0.07 | 0.0701 | 0.0701 | 0.0701 | 0.1291 | 0.258 | 0.31 | 0.1782 | 0.0891 | 0.0742 | 0.064 | 0.062707 | 1.966 | 0.0778 | 7 | 0.004041 | 900 kcmil CU- HH Hollow |  | 900 kcmil CU- HH Hollow | 23.7134 | 49.9364 | 75 | 0.038964 | 1.505 | 0.047624
CU- HH Hollow | 850000 | [10 empty] | 0.14 | 1.901 | 36710 | 13730 | 1450 | 0.0751 | 0.0677 | 0.0678 | 0.0678 | 0.0678 | 0.0741 | 0.0742 | 0.0742 | 0.0742 | 0.1309 | 0.262 | 0.314 | 0.1805 | 0.0903 | 0.0752 | 0.0677 | 0.066332 | 1.901 | 0.0751 | 7 | 0.004041 | 850 kcmil CU- HH Hollow |  | 850 kcmil CU- HH Hollow | 22.8905 | 48.2854 | 75 | 0.041217 | 1.45 | 0.050378
CU- HH Hollow | 800000 | [10 empty] | 0.137 | 1.82 | 34550 | 12920 | 1390 | 0.0722 | 0.072 | 0.072 | 0.072 | 0.0721 | 0.0788 | 0.0788 | 0.0788 | 0.0788 | 0.1329 | 0.266 | 0.319 | 0.1833 | 0.0917 | 0.0764 | 0.072 | 0.070545 | 1.82 | 0.0722 | 7 | 0.004041 | 800 kcmil CU- HH Hollow |  | 800 kcmil CU- HH Hollow | 22.0066 | 46.228 | 75 | 0.043835 | 1.39 | 0.053577
CU- HH Hollow | 790000 | [10 empty] | 0.131 | 1.65 | 34120 | 12760 | 1335 | 0.0646 | 0.0729 | 0.0729 | 0.073 | 0.073 | 0.0797 | 0.0798 | 0.0799 | 0.0799 | 0.1385 | 0.277 | 0.332 | 0.1906 | 0.0953 | 0.0794 | 0.0729 | 0.071427 | 1.65 | 0.0646 | 7 | 0.004041 | 790 kcmil CU- HH Hollow |  | 790 kcmil CU- HH Hollow | 19.6901 | 41.91 | 75 | 0.044383 | 1.335 | 0.054247
CU- HH Hollow | 750000 | [10 empty] | 0.133 | 1.75 | 32390 | 12120 | 1325 | 0.0691 | 0.0768 | 0.0768 | 0.0768 | 0.0769 | 0.084 | 0.084 | 0.0841 | 0.0841 | 0.1351 | 0.27 | 0.324 | 0.1864 | 0.0932 | 0.0777 | 0.0768 | 0.075248 | 1.75 | 0.0691 | 7 | 0.004041 | 750 kcmil CU- HH Hollow |  | 750 kcmil CU- HH Hollow | 21.0617 | 44.45 | 75 | 0.046757 | 1.325 | 0.057149
CU- HH Hollow | 700000 | [10 empty] | 0.13 | 1.686 | 30230 | 11310 | 1265 | 0.0665 | 0.0822 | 0.0823 | 0.0823 | 0.0823 | 0.09 | 0.09 | 0.0901 | 0.0901 | 0.137 | 0.274 | 0.329 | 0.1891 | 0.0945 | 0.0788 | 0.0822 | 0.080539 | 1.686 | 0.0665 | 7 | 0.004041 | 700 kcmil CU- HH Hollow |  | 700 kcmil CU- HH Hollow | 20.2692 | 42.8244 | 75 | 0.050045 | 1.265 | 0.061167
CU- HH Hollow | 650000 | [10 empty] | 0.126 | 1.61 | 28070 | 10500 | 1200 | 0.0635 | 0.0886 | 0.0886 | 0.0886 | 0.0887 | 0.0969 | 0.097 | 0.097 | 0.097 | 0.1394 | 0.279 | 0.335 | 0.1924 | 0.0962 | 0.0802 | 0.0886 | 0.08681 | 1.61 | 0.0635 | 7 | 0.004041 | 650 kcmil CU- HH Hollow |  | 650 kcmil CU- HH Hollow | 19.3548 | 40.894 | 75 | 0.053941 | 1.2 | 0.06593
CU- HH Hollow | 600000 | [10 empty] | 0.123 | 1.558 | 25910 | 9692 | 1140 | 0.0615 | 0.0959 | 0.096 | 0.096 | 0.096 | 0.105 | 0.1051 | 0.1051 | 0.1051 | 0.141 | 0.282 | 0.338 | 0.1947 | 0.0974 | 0.0811 | 0.0959 | 0.093962 | 1.558 | 0.0615 | 7 | 0.004041 | 600 kcmil CU- HH Hollow |  | 600 kcmil CU- HH Hollow | 18.7452 | 39.5732 | 75 | 0.058385 | 1.14 | 0.071362
CU- HH Hollow | 550000 | [10 empty] | 0.119 | 1.478 | 23750 | 8884 | 1075 | 0.0583 | 0.1047 | 0.1048 | 0.1048 | 0.1048 | 0.1146 | 0.1146 | 0.1147 | 0.1147 | 0.1437 | 0.287 | 0.345 | 0.1985 | 0.0992 | 0.0827 | 0.1047 | 0.10258 | 1.478 | 0.0583 | 7 | 0.004041 | 550 kcmil CU- HH Hollow |  | 550 kcmil CU- HH Hollow | 17.7698 | 37.5412 | 75 | 0.063743 | 1.075 | 0.07791
CU- HH Hollow | 512000 | [10 empty] | 0.115 | 1.4 | 22110 | 8270 | 1020 | 0.0551 | 0.1124 | 0.1125 | 0.1125 | 0.1125 | 0.123 | 0.123 | 0.1231 | 0.1231 | 0.1466 | 0.293 | 0.352 | 0.202 | 0.1012 | 0.0843 | 0.1124 | 0.11013 | 1.4 | 0.0551 | 7 | 0.004041 | 512 kcmil CU- HH Hollow |  | 512 kcmil CU- HH Hollow | 16.7945 | 35.56 | 75 | 0.068431 | 1.02 | 0.08364
CU- HH Hollow | 500000 | [10 empty] | 0.115 | 1.39 | 21590 | 8076 | 1005 | 0.0547 | 0.1151 | 0.1151 | 0.1152 | 0.1152 | 0.1259 | 0.126 | 0.126 | 0.126 | 0.1469 | 0.294 | 0.353 | 0.203 | 0.1014 | 0.0845 | 0.1151 | 0.11277 | 1.39 | 0.0547 | 7 | 0.004041 | 500 kcmil CU- HH Hollow | 1 | 500 kcmil CU- HH Hollow - 1 | 16.6726 | 35.306 | 75 | 0.070075 | 1.005 | 0.085649
CU- HH Hollow | 500000 | [10 empty] | 0.109 | 1.268 | 21590 | 8074 | 978 | 0.0494 | 0.1151 | 0.1152 | 0.1152 | 0.1152 | 0.1259 | 0.126 | 0.126 | 0.1261 | 0.1521 | 0.304 | 0.365 | 0.209 | 0.1047 | 0.0872 | 0.1151 | 0.11277 | 1.268 | 0.0494 | 7 | 0.004041 | 500 kcmil CU- HH Hollow | 2 | 500 kcmil CU- HH Hollow - 2 | 15.0571 | 32.2072 | 75 | 0.070075 | 0.978 | 0.085649
CU- HH Hollow | 500000 | [10 empty] | 0.13 | 1.1 | 21590 | 8068 | 937 | 0.042 | 0.115 | 0.1151 | 0.1152 | 0.1153 | 0.1258 | 0.1259 | 0.126 | 0.126 | 0.1603 | 0.321 | 0.385 | 0.219 | 0.1098 | 0.0915 | 0.115 | 0.11268 | 1.1 | 0.042 | 7 | 0.004041 | 500 kcmil CU- HH Hollow | 3 | 500 kcmil CU- HH Hollow - 3 | 12.8016 | 27.94 | 75 | 0.070014 | 0.937 | 0.085575
CU- HH Hollow | 500000 | [10 empty] | 0.144 | 1.02 | 21590 | 8063 | 915 | 0.0384 | 0.115 | 0.115 | 0.1152 | 0.1152 | 0.1258 | 0.1259 | 0.126 | 0.1261 | 0.1648 | 0.33 | 0.396 | 0.225 | 0.1124 | 0.0937 | 0.115 | 0.11268 | 1.02 | 0.0384 | 7 | 0.004041 | 500 kcmil CU- HH Hollow | 4 | 500 kcmil CU- HH Hollow - 4 | 11.7043 | 25.908 | 75 | 0.070014 | 0.915 | 0.085575
CU- HH Hollow | 450000 | [10 empty] | 0.111 | 1.317 | 19430 | 7268 | 939 | 0.0518 | 0.1279 | 0.128 | 0.128 | 0.128 | 0.14 | 0.1401 | 0.1401 | 0.1401 | 0.1496 | 0.299 | 0.359 | 0.207 | 0.1033 | 0.0861 | 0.1279 | 0.12532 | 1.317 | 0.0518 | 7 | 0.004041 | 450 kcmil CU- HH Hollow | 1 | 450 kcmil CU- HH Hollow - 1 | 15.7886 | 33.4518 | 75 | 0.077868 | 0.939 | 0.095174
CU- HH Hollow | 450000 | [10 empty] | 0.105 | 1.188 | 19430 | 7266 | 910 | 0.0462 | 0.1278 | 0.1279 | 0.1279 | 0.128 | 0.1399 | 0.14 | 0.14 | 0.1401 | 0.1554 | 0.311 | 0.373 | 0.214 | 0.107 | 0.0892 | 0.1278 | 0.12522 | 1.188 | 0.0462 | 7 | 0.004041 | 450 kcmil CU- HH Hollow | 2 | 450 kcmil CU- HH Hollow - 2 | 14.0818 | 30.1752 | 75 | 0.077807 | 0.91 | 0.0951
CU- HH Hollow | 400000 | [10 empty] | 0.106 | 1.218 | 17270 | 6460 | 864 | 0.0478 | 0.1439 | 0.144 | 0.144 | 0.144 | 0.1575 | 0.1576 | 0.1576 | 0.1576 | 0.1537 | 0.307 | 0.369 | 0.212 | 0.1061 | 0.0884 | 0.1439 | 0.14099 | 1.218 | 0.0478 | 7 | 0.004041 | 400 kcmil CU- HH Hollow | 1 | 400 kcmil CU- HH Hollow - 1 | 14.5694 | 30.9372 | 75 | 0.087609 | 0.864 | 0.10708
CU- HH Hollow | 400000 | [10 empty] | 0.1 | 1.103 | 17270 | 6458 | 838 | 0.0428 | 0.1438 | 0.1439 | 0.1439 | 0.144 | 0.1574 | 0.1575 | 0.1575 | 0.1576 | 0.1593 | 0.319 | 0.382 | 0.219 | 0.1097 | 0.0914 | 0.1438 | 0.14089 | 1.103 | 0.0428 | 7 | 0.004041 | 400 kcmil CU- HH Hollow | 2 | 400 kcmil CU- HH Hollow - 2 | 13.0454 | 28.0162 | 75 | 0.087548 | 0.838 | 0.10701
CU- HH Hollow | 350000 | [10 empty] | 0.102 | 1.128 | 15110 | 5653 | 790 | 0.0443 | 0.1644 | 0.1645 | 0.1645 | 0.1645 | 0.1799 | 0.18 | 0.18 | 0.18 | 0.1576 | 0.315 | 0.378 | 0.218 | 0.1089 | 0.0907 | 0.1644 | 0.16108 | 1.128 | 0.0443 | 7 | 0.004041 | 350 kcmil CU- HH Hollow | 1 | 350 kcmil CU- HH Hollow - 1 | 13.5026 | 28.6512 | 75 | 0.10009 | 0.79 | 0.12233
CU- HH Hollow | 350000 | [10 empty] | 0.096 | 1.014 | 15110 | 5650 | 764 | 0.0393 | 0.1644 | 0.1645 | 0.1645 | 0.1646 | 0.1799 | 0.18 | 0.18 | 0.1801 | 0.1637 | 0.328 | 0.393 | 0.225 | 0.1127 | 0.0939 | 0.1644 | 0.16108 | 1.014 | 0.0393 | 7 | 0.004041 | 350 kcmil CU- HH Hollow | 2 | 350 kcmil CU- HH Hollow - 2 | 11.9786 | 25.7556 | 75 | 0.10009 | 0.764 | 0.12233
CU- HH Hollow | 300000 | [10 empty] | 0.096 | 1.02 | 12950 | 4845 | 709 | 0.0399 | 0.1918 | 0.1919 | 0.1919 | 0.1919 | 0.21 | 0.21 | 0.21 | 0.21 | 0.1628 | 0.326 | 0.391 | 0.225 | 0.1124 | 0.0937 | 0.1918 | 0.18792 | 1.02 | 0.0399 | 7 | 0.004041 | 300 kcmil CU- HH Hollow | 1 | 300 kcmil CU- HH Hollow - 1 | 12.1615 | 25.908 | 75 | 0.11677 | 0.709 | 0.14272
CU- HH Hollow | 300000 | [10 empty] | 0.091 | 0.919 | 12950 | 4843 | 687 | 0.0355 | 0.1917 | 0.1918 | 0.1918 | 0.1919 | 0.21 | 0.21 | 0.21 | 0.21 | 0.1688 | 0.338 | 0.405 | 0.232 | 0.1162 | 0.0968 | 0.1917 | 0.18783 | 0.919 | 0.0355 | 7 | 0.004041 | 300 kcmil CU- HH Hollow | 2 | 300 kcmil CU- HH Hollow - 2 | 10.8204 | 23.3426 | 75 | 0.11671 | 0.687 | 0.14265
CU- HH Hollow | 250000 | [10 empty] | 0.091 | 0.914 | 10790 | 4037 | 626 | 0.0357 | 0.23 | 0.23 | 0.23 | 0.23 | 0.252 | 0.252 | 0.252 | 0.252 | 0.1685 | 0.337 | 0.404 | 0.233 | 0.1163 | 0.097 | 0.23 | 0.22535 | 0.914 | 0.0357 | 7 | 0.004041 | 250 kcmil CU- HH Hollow | 1 | 250 kcmil CU- HH Hollow - 1 | 10.8814 | 23.2156 | 75 | 0.14003 | 0.626 | 0.17115
CU- HH Hollow | 250000 | [10 empty] | 0.086 | 0.818 | 10790 | 4036 | 606 | 0.0315 | 0.23 | 0.23 | 0.23 | 0.23 | 0.252 | 0.252 | 0.252 | 0.252 | 6.1748 | 0.35 | 0.42 | 0.241 | 0.1203 | 0.1002 | 0.23 | 0.22535 | 0.818 | 0.0315 | 7 | 0.004041 | 250 kcmil CU- HH Hollow | 2 | 250 kcmil CU- HH Hollow - 2 | 9.6012 | 20.7772 | 75 | 0.14003 | 0.606 | 0.17115
CU- HH Hollow | 250000 | [10 empty] | 0.094 | 0.766 | 10790 | 4034 | 594 | 0.0292 | 0.23 | 0.23 | 0.23 | 0.23 | 0.252 | 0.252 | 0.252 | 0.252 | 0.1787 | 0.357 | 0.429 | 0.245 | 0.1226 | 0.1022 | 0.23 | 0.22535 | 0.766 | 0.0292 | 7 | 0.004041 | 250 kcmil CU- HH Hollow | 3 | 250 kcmil CU- HH Hollow - 3 | 8.9002 | 19.4564 | 75 | 0.14003 | 0.594 | 0.17115
CU- HH Hollow | 214500 | [10 empty] | 0.098 | 0.65 | 9265 | 3459 | 524 | 0.0243 | 0.268 | 0.268 | 0.268 | 0.268 | 0.293 | 0.293 | 0.293 | 0.294 | 0.1879 | 0.376 | 0.451 | 0.257 | 0.1285 | 0.1071 | 0.268 | 0.26259 | 0.65 | 0.0243 | 7 | 0.004041 | 214.5 kcmil CU- HH Hollow |  | 214.5 kcmil CU- HH Hollow | 7.4066 | 16.51 | 75 | 0.16316 | 0.524 | 0.19943
CU- HH Hollow | 4/0 | 4/0 | [9 empty] | 0.082 | 0.733 | 9140 | 3415 | 539 | 0.0281 | 0.272 | 0.272 | 0.272 | 0.272 | 0.297 | 0.297 | 0.298 | 0.298 | 0.1806 | 0.361 | 0.433 | 0.248 | 0.1242 | 0.1035 | 0.272 | 0.2665 | 0.733 | 0.0281 | 7 | 0.004041 | 4/0 CU- HH Hollow |  | 4/0 CU- HH Hollow | 8.5649 | 18.6182 | 75 | 0.1656 | 0.539 | 0.2024
CU- HH Hollow | 3/0 | 3/0 | [9 empty] | 0.08 | 0.608 | 7240 | 2707 | 454 | 0.023 | 0.343 | 0.343 | 0.343 | 0.343 | 0.375 | 0.375 | 0.375 | 0.375 | 0.1907 | 0.381 | 0.458 | 0.262 | 0.1309 | 0.1091 | 0.343 | 0.33607 | 0.608 | 0.023 | 7 | 0.004041 | 3/0 CU- HH Hollow |  | 3/0 CU- HH Hollow | 7.0104 | 15.4432 | 75 | 0.20882 | 0.454 | 0.25524
CU- HH Hollow | 2/0 | 2/0 | [9 empty] | 0.08 | 0.5 | 5750 | 2146 | 382 | 0.018 | 0.432 | 0.432 | 0.432 | 0.432 | 0.472 | 0.473 | 0.473 | 0.473 | 0.201 | 0.403 | 0.483 | 0.276 | 0.1378 | 0.1149 | 0.432 | 0.42327 | 0.5 | 0.018 | 7 | 0.004041 | 2/0 CU- HH Hollow |  | 2/0 CU- HH Hollow | 5.4864 | 12.7 | 75 | 0.26301 | 0.382 | 0.32146
AL- Alcoa Hard Drawn | 6 | 6 | [6 empty] | 7 | 0.0612 |  |  | 0.184 | 528 | 130 | 100 | 0.00556 | 3.56 | 3.56 | 3.56 | 3.56 | 3.91 | 3.91 | 3.91 | 3.91 | 0.2626 | 0.5251 | 0.6301 | 0.3468 | 0.1734 | 0.1445 | 3.56 | 3.4833 | 0.184 | 0.00556 | 2 | 0.004308 | 6 AL- Alcoa Hard Drawn (7) |  | 6 AL- Alcoa Hard Drawn (7) | 1.6947 | 4.6736 | 90 | 2.1644 | 0.1 | 2.8171
AL- Alcoa Hard Drawn | 4 | 4 | [6 empty] | 7 | 0.0772 |  |  | 0.232 | 826 | 207 | 134 | 0.007 | 2.24 | 2.24 | 2.24 | 2.24 | 2.46 | 2.46 | 2.46 | 2.46 | 0.2509 | 0.5017 | 0.6201 | 0.3302 | 0.1651 | 0.1376 | 2.24 | 2.1918 | 0.232 | 0.007 | 2 | 0.004308 | 4 AL- Alcoa Hard Drawn (7) |  | 4 AL- Alcoa Hard Drawn (7) | 2.1336 | 5.8928 | 90 | 1.3619 | 0.134 | 1.7726
AL- Alcoa Hard Drawn | 3 | 3 | [6 empty] | 7 | 0.0867 |  |  | 0.26 | 1022 | 261 | 155 | 0.00787 | 1.77 | 1.77 | 1.77 | 1.77 | 1.95 | 1.95 | 1.95 | 1.95 | 0.245 | 0.4899 | 0.5879 | 0.3221 | 0.161 | 0.1342 | 1.77 | 1.7319 | 0.26 | 0.00787 | 2 | 0.004308 | 3 AL- Alcoa Hard Drawn (7) |  | 3 AL- Alcoa Hard Drawn (7) | 2.3988 | 6.604 | 90 | 1.0761 | 0.155 | 1.4007
AL- Alcoa Hard Drawn | 2 | 2 | [6 empty] | 7 | 0.0974 |  |  | 0.292 | 1266 | 329 | 180 | 0.00883 | 1.41 | 1.41 | 1.41 | 1.41 | 1.55 | 1.55 | 1.55 | 1.55 | 0.2391 | 0.4782 | 0.5739 | 0.3139 | 0.157 | 0.1308 | 1.41 | 1.3796 | 0.292 | 0.00883 | 2 | 0.004308 | 2 AL- Alcoa Hard Drawn (7) |  | 2 AL- Alcoa Hard Drawn (7) | 2.6914 | 7.4168 | 90 | 0.85726 | 0.18 | 1.1158
AL- Alcoa Hard Drawn | 1 | 1 | [6 empty] | 7 | 0.1094 |  |  | 0.328 | 1537 | 414 | 209 | 0.00992 | 1.12 | 1.12 | 1.12 | 1.12 | 1.23 | 1.23 | 1.23 | 1.23 | 0.2333 | 0.4665 | 0.5598 | 0.3055 | 0.1528 | 0.1273 | 1.12 | 1.0959 | 0.328 | 0.00992 | 2 | 0.004308 | 1 AL- Alcoa Hard Drawn (7) |  | 1 AL- Alcoa Hard Drawn (7) | 3.0236 | 8.3312 | 90 | 0.68095 | 0.209 | 0.88629
AL- Alcoa Hard Drawn | 1/0 | 1/0 | [6 empty] | 7 | 0.1228 |  |  | 0.368 | 1865 | 523 | 242 | 0.01113 | 0.885 | 0.8851 | 0.8853 | 0.885 | 0.973 | 0.9731 | 0.9732 | 0.973 | 0.2264 | 0.4528 | 0.5434 | 0.2976 | 0.1488 | 0.124 | 0.885 | 0.86594 | 0.368 | 0.01113 | 2 | 0.004308 | 1/0 AL- Alcoa Hard Drawn (7) |  | 1/0 AL- Alcoa Hard Drawn (7) | 3.3924 | 9.3472 | 90 | 0.53807 | 0.242 | 0.70033
AL- Alcoa Hard Drawn | 1/0 | 1/0 | [6 empty] | 19 | 0.0745 |  |  | 0.373 | 2090 | 523 | 244 | 0.01177 | 0.885 | 0.8851 | 0.8853 | 0.885 | 0.973 | 0.9731 | 0.9732 | 0.973 | 0.2246 | 0.4492 | 0.5391 | 0.2964 | 0.1482 | 0.1235 | 0.885 | 0.86594 | 0.373 | 0.01177 | 2 | 0.004308 | 1/0 AL- Alcoa Hard Drawn (19) |  | 1/0 AL- Alcoa Hard Drawn (19) | 3.5875 | 9.4742 | 90 | 0.53807 | 0.244 | 0.70033
AL- Alcoa Hard Drawn | 2/0 | 2/0 | [6 empty] | 7 | 0.1379 |  |  | 0.414 | 2350 | 659 | 282 | 0.01251 | 0.702 | 0.7021 | 0.7024 | 0.702 | 0.771 | 0.7711 | 0.7713 | 0.771 | 0.2216 | 0.4431 | 0.5317 | 0.289 | 0.1445 | 0.1204 | 0.702 | 0.68688 | 0.414 | 0.01251 | 2 | 0.004308 | 2/0 AL- Alcoa Hard Drawn (7) |  | 2/0 AL- Alcoa Hard Drawn (7) | 3.813 | 10.5156 | 90 | 0.42681 | 0.282 | 0.55551
AL- Alcoa Hard Drawn | 2/0 | 2/0 | [6 empty] | 19 | 0.0837 |  |  | 0.419 | 2586 | 659 | 283 | 0.01321 | 0.702 | 0.7021 | 0.7024 | 0.702 | 0.771 | 0.7711 | 0.7713 | 0.771 | 0.2188 | 0.4376 | 0.5251 | 0.2882 | 0.1441 | 0.1201 | 0.702 | 0.68688 | 0.419 | 0.01321 | 2 | 0.004308 | 2/0 AL- Alcoa Hard Drawn (19) |  | 2/0 AL- Alcoa Hard Drawn (19) | 4.0264 | 10.6426 | 90 | 0.42681 | 0.283 | 0.55551
AL- Alcoa Hard Drawn | 3/0 | 3/0 | [6 empty] | 7 | 0.1548 |  |  | 0.464 | 2845 | 832 | 327 | 0.01404 | 0.557 | 0.5571 | 0.5574 | 0.558 | 0.612 | 0.6121 | 0.6124 | 0.613 | 0.2157 | 0.4314 | 0.5177 | 0.281 | 0.1405 | 0.1171 | 0.557 | 0.545 | 0.464 | 0.01404 | 2 | 0.004308 | 3/0 AL- Alcoa Hard Drawn (7) |  | 3/0 AL- Alcoa Hard Drawn (7) | 4.2794 | 11.7856 | 90 | 0.33865 | 0.327 | 0.44077
AL- Alcoa Hard Drawn | 3/0 | 3/0 | [6 empty] | 19 | 0.094 |  |  | 0.47 | 3200 | 832 | 328 | 0.01483 | 0.557 | 0.5571 | 0.5574 | 0.558 | 0.612 | 0.6121 | 0.6124 | 0.613 | 0.2129 | 0.4258 | 0.511 | 0.2801 | 0.14 | 0.1167 | 0.557 | 0.545 | 0.47 | 0.01483 | 2 | 0.004308 | 3/0 AL- Alcoa Hard Drawn (19) |  | 3/0 AL- Alcoa Hard Drawn (19) | 4.5202 | 11.938 | 90 | 0.33865 | 0.328 | 0.44077
AL- Alcoa Hard Drawn | 4/0 | 4/0 | [6 empty] | 7 | 0.1739 |  |  | 0.522 | 3590 | 1049 | 380 | 0.01577 | 0.441 | 0.4411 | 0.4415 | 0.442 | 0.485 | 0.4851 | 0.4855 | 0.486 | 0.2099 | 0.4196 | 0.5036 | 0.2726 | 0.1363 | 0.1136 | 0.441 | 0.4315 | 0.522 | 0.01577 | 2 | 0.004308 | 4/0 AL- Alcoa Hard Drawn (7) |  | 4/0 AL- Alcoa Hard Drawn (7) | 4.8067 | 13.2588 | 90 | 0.26812 | 0.38 | 0.34898
AL- Alcoa Hard Drawn | 4/0 | 4/0 | [6 empty] | 19 | 0.1055 |  |  | 0.528 | 3890 | 1049 | 381 | 0.01666 | 0.441 | 0.4411 | 0.4415 | 0.442 | 0.485 | 0.4851 | 0.4855 | 0.486 | 0.2071 | 0.4141 | 0.4969 | 0.2717 | 0.1358 | 0.1132 | 0.441 | 0.4315 | 0.528 | 0.01666 | 2 | 0.004308 | 4/0 AL- Alcoa Hard Drawn (19) |  | 4/0 AL- Alcoa Hard Drawn (19) | 5.078 | 13.4112 | 90 | 0.26812 | 0.381 | 0.34898
AL- Alcoa Hard Drawn | 250000 | [7 empty] | 37 | 0.0822 |  |  | 0.575 | 4860 | 1239 | 425 | 0.01841 | 0.374 | 0.3741 | 0.3746 | 0.375 | 0.411 | 0.4111 | 0.4115 | 0.412 | 0.202 | 0.404 | 0.4848 | 0.2657 | 0.1328 | 0.1107 | 0.374 | 0.36594 | 0.575 | 0.01841 | 2 | 0.004308 | 250 kcmil AL- Alcoa Hard Drawn (37) |  | 250 kcmil AL- Alcoa Hard Drawn (37) | 5.6114 | 14.605 | 90 | 0.22739 | 0.425 | 0.29596
AL- Alcoa Hard Drawn | 266800 | [7 empty] | 7 | 0.1953 |  |  | 0.586 | 4525 | 1322 | 441 | 0.01771 | 0.35 | 0.3502 | 0.3506 | 0.351 | 0.385 | 0.3852 | 0.3855 | 0.386 | 0.204 | 0.4079 | 0.4895 | 0.2642 | 0.1321 | 0.1101 | 0.35 | 0.34246 | 0.586 | 0.01771 | 2 | 0.004308 | 266.8 kcmil AL- Alcoa Hard Drawn (7) |  | 266.8 kcmil AL- Alcoa Hard Drawn (7) | 5.398 | 14.8844 | 90 | 0.2128 | 0.441 | 0.27697
AL- Alcoa Hard Drawn | 266800 | [7 empty] | 37 | 0.0849 |  |  | 0.594 | 5180 | 1322 | 443 | 0.01902 | 0.35 | 0.3502 | 0.3506 | 0.351 | 0.385 | 0.3852 | 0.3855 | 0.386 | 0.2004 | 0.4007 | 0.4809 | 0.2633 | 0.1316 | 0.1097 | 0.35 | 0.34246 | 0.594 | 0.01902 | 2 | 0.004308 | 266.8 kcmil AL- Alcoa Hard Drawn (37) |  | 266.8 kcmil AL- Alcoa Hard Drawn (37) | 5.7973 | 15.0876 | 90 | 0.2128 | 0.443 | 0.27697
AL- Alcoa Hard Drawn | 300000 | [7 empty] | 19 | 0.1257 |  |  | 0.629 | 5300 | 1487 | 478 | 0.01983 | 0.311 | 0.3112 | 0.3117 | 0.312 | 0.342 | 0.3422 | 0.3426 | 0.343 | 0.1983 | 0.3965 | 0.4758 | 0.2592 | 0.1296 | 0.108 | 0.311 | 0.3043 | 0.629 | 0.01983 | 2 | 0.004308 | 300 kcmil AL- Alcoa Hard Drawn (19) |  | 300 kcmil AL- Alcoa Hard Drawn (19) | 6.0442 | 15.9766 | 90 | 0.18908 | 0.478 | 0.2461
AL- Alcoa Hard Drawn | 300000 | [7 empty] | 37 | 0.09 |  |  | 0.63 | 5830 | 1487 | 478 | 0.02017 | 0.311 | 0.3112 | 0.3117 | 0.312 | 0.342 | 0.3422 | 0.3426 | 0.343 | 0.1974 | 0.3947 | 0.4737 | 0.2592 | 0.1296 | 0.108 | 0.311 | 0.3043 | 0.63 | 0.02017 | 2 | 0.004308 | 300 kcmil AL- Alcoa Hard Drawn (37) |  | 300 kcmil AL- Alcoa Hard Drawn (37) | 6.1478 | 16.002 | 90 | 0.18908 | 0.478 | 0.2461
AL- Alcoa Hard Drawn | 336400 | [7 empty] | 19 | 0.1331 |  |  | 0.666 | 5940 | 1667 | 514 | 0.021 | 0.278 | 0.2782 | 0.2788 | 0.279 | 0.306 | 0.3062 | 0.3067 | 0.307 | 0.1953 | 0.3907 | 0.4688 | 0.2551 | 0.1276 | 0.1063 | 0.278 | 0.27201 | 0.666 | 0.021 | 2 | 0.004308 | 336.4 kcmil AL- Alcoa Hard Drawn (19) |  | 336.4 kcmil AL- Alcoa Hard Drawn (19) | 6.4008 | 16.9164 | 90 | 0.16902 | 0.514 | 0.21999
AL- Alcoa Hard Drawn | 336400 | [7 empty] | 37 | 0.0954 |  |  | 0.668 | 6400 | 1667 | 514 | 0.02135 | 0.278 | 0.2782 | 0.2788 | 0.279 | 0.306 | 0.3062 | 0.3067 | 0.307 | 0.1945 | 0.389 | 0.4668 | 0.2549 | 0.1274 | 0.1062 | 0.278 | 0.27201 | 0.668 | 0.02135 | 2 | 0.004308 | 336.4 kcmil AL- Alcoa Hard Drawn (37) |  | 336.4 kcmil AL- Alcoa Hard Drawn (37) | 6.5075 | 16.9672 | 90 | 0.16902 | 0.514 | 0.21999
AL- Alcoa Hard Drawn | 350000 | [7 empty] | 37 | 0.0973 |  |  | 0.681 | 6680 | 1735 | 528 | 0.02178 | 0.267 | 0.2672 | 0.2678 | 0.268 | 0.294 | 0.2942 | 0.2947 | 0.295 | 0.1935 | 0.387 | 0.4644 | 0.2537 | 0.1268 | 0.1057 | 0.267 | 0.26125 | 0.681 | 0.02178 | 2 | 0.004308 | 350 kcmil AL- Alcoa Hard Drawn (37) |  | 350 kcmil AL- Alcoa Hard Drawn (37) | 6.6385 | 17.2974 | 90 | 0.16233 | 0.528 | 0.21129
AL- Alcoa Hard Drawn | 397500 | [7 empty] | 19 | 0.1447 |  |  | 0.724 | 6880 | 1967 | 575 | 0.02283 | 0.235 | 0.2352 | 0.2359 | 0.236 | 0.258 | 0.2582 | 0.2589 | 0.259 | 0.1911 | 0.3822 | 0.4587 | 0.2491 | 0.1246 | 0.1038 | 0.235 | 0.22994 | 0.724 | 0.02283 | 2 | 0.004308 | 397.5 kcmil AL- Alcoa Hard Drawn (19) |  | 397.5 kcmil AL- Alcoa Hard Drawn (19) | 6.9586 | 18.3896 | 90 | 0.14288 | 0.575 | 0.18596
AL- Alcoa Hard Drawn | 477000 | [7 empty] | 19 | 0.1585 |  |  | 0.793 | 8090 | 2364 | 646 | 0.02501 | 0.196 | 0.1963 | 0.1971 | 0.198 | 0.215 | 0.2153 | 0.216 | 0.216 | 0.1865 | 0.373 | 0.4476 | 0.2429 | 0.1214 | 0.1012 | 0.196 | 0.19178 | 0.793 | 0.02501 | 2 | 0.004308 | 477 kcmil AL- Alcoa Hard Drawn (19) |  | 477 kcmil AL- Alcoa Hard Drawn (19) | 7.623 | 20.1422 | 90 | 0.11917 | 0.646 | 0.1551
AL- Alcoa Hard Drawn | 500000 | [7 empty] | 19 | 0.1623 |  |  | 0.812 | 8475 | 2478 | 664 | 0.0256 | 0.187 | 0.1873 | 0.1882 | 0.189 | 0.206 | 0.2062 | 0.207 | 0.208 | 0.1853 | 0.3707 | 0.4448 | 0.2412 | 0.1206 | 0.1005 | 0.187 | 0.18297 | 0.812 | 0.0256 | 2 | 0.004308 | 500 kcmil AL- Alcoa Hard Drawn (19) |  | 500 kcmil AL- Alcoa Hard Drawn (19) | 7.8029 | 20.6248 | 90 | 0.11369 | 0.664 | 0.14798
AL- Alcoa Hard Drawn | 500000 | [7 empty] | 37 | 0.1162 |  |  | 0.813 | 9010 | 2478 | 664 | 0.02603 | 0.187 | 0.1873 | 0.1882 | 0.189 | 0.206 | 0.2062 | 0.207 | 0.208 | 0.1845 | 0.3689 | 0.4427 | 0.241 | 0.1205 | 0.1004 | 0.187 | 0.18297 | 0.813 | 0.02603 | 2 | 0.004308 | 500 kcmil AL- Alcoa Hard Drawn (37) |  | 500 kcmil AL- Alcoa Hard Drawn (37) | 7.9339 | 20.6502 | 90 | 0.11369 | 0.664 | 0.14798
AL- Alcoa Hard Drawn | 556500 | [7 empty] | 19 | 0.1711 |  |  | 0.856 | 9440 | 2758 | 710 | 0.02701 | 0.168 | 0.1683 | 0.1693 | 0.17 | 0.185 | 0.1853 | 0.1862 | 0.187 | 0.1826 | 0.3652 | 0.4383 | 0.2374 | 0.1187 | 0.0989 | 0.168 | 0.16438 | 0.856 | 0.02701 | 2 | 0.004308 | 556.5 kcmil AL- Alcoa Hard Drawn (19) |  | 556.5 kcmil AL- Alcoa Hard Drawn (19) | 8.2326 | 21.7424 | 90 | 0.10214 | 0.71 | 0.13294
AL- Alcoa Hard Drawn | 636000 | [7 empty] | 37 | 0.1311 |  |  | 0.918 | 11240 | 3152 | 776 | 0.02936 | 0.147 | 0.1474 | 0.1484 | 0.149 | 0.162 | 0.1623 | 0.1633 | 0.164 | 0.1785 | 0.3569 | 0.4283 | 0.2323 | 0.1162 | 0.0968 | 0.147 | 0.14383 | 0.918 | 0.02936 | 2 | 0.004308 | 636 kcmil AL- Alcoa Hard Drawn (37) |  | 636 kcmil AL- Alcoa Hard Drawn (37) | 8.9489 | 23.3172 | 90 | 0.089374 | 0.776 | 0.11633
AL- Alcoa Hard Drawn | 715500 | [7 empty] | 37 | 0.1391 |  |  | 0.974 | 12640 | 3546 | 817 | 0.03114 | 0.137 | 0.1314 | 0.1326 | 0.133 | 0.144 | 0.1444 | 0.1455 | 0.146 | 0.1754 | 0.3508 | 0.421 | 0.2282 | 0.1141 | 0.0951 | 0.137 | 0.13405 | 0.974 | 0.03114 | 2 | 0.004308 | 715.5 kcmil AL- Alcoa Hard Drawn (37) |  | 715.5 kcmil AL- Alcoa Hard Drawn (37) | 9.4915 | 24.7396 | 90 | 0.083294 | 0.817 | 0.10841
AL- Alcoa Hard Drawn | 750000 | [7 empty] | 37 | 0.1424 |  |  | 0.997 | 12980 | 3717 | 864 | 0.03188 | 0.125 | 0.1254 | 0.1267 | 0.127 | 0.137 | 0.1374 | 0.1385 | 0.139 | 0.1743 | 0.3485 | 0.4182 | 0.2266 | 0.1133 | 0.0944 | 0.125 | 0.12231 | 0.997 | 0.03188 | 2 | 0.004308 | 750 kcmil AL- Alcoa Hard Drawn (37) |  | 750 kcmil AL- Alcoa Hard Drawn (37) | 9.717 | 25.3238 | 90 | 0.075998 | 0.864 | 0.098916
AL- Alcoa Hard Drawn | 750000 | [7 empty] | 61 | 0.1109 |  |  | 0.998 | 13510 | 3717 | 864 | 0.03211 | 0.125 | 0.1254 | 0.1267 | 0.127 | 0.137 | 0.1374 | 0.1385 | 0.139 | 0.1739 | 0.3477 | 0.4173 | 0.2263 | 0.1132 | 0.0943 | 0.125 | 0.12231 | 0.998 | 0.03211 | 2 | 0.004308 | 750 kcmil AL- Alcoa Hard Drawn (61) |  | 750 kcmil AL- Alcoa Hard Drawn (61) | 9.7871 | 25.3492 | 90 | 0.075998 | 0.864 | 0.098916
AL- Alcoa Hard Drawn | 795000 | [7 empty] | 37 | 0.1466 |  |  | 1.026 | 13770 | 3940 | 897 | 0.03283 | 0.117 | 0.1175 | 0.1188 | 0.12 | 0.129 | 0.1294 | 0.1306 | 0.131 | 0.1728 | 0.3455 | 0.4146 | 0.2244 | 0.1122 | 0.0935 | 0.117 | 0.11448 | 1.026 | 0.03283 | 2 | 0.004308 | 795 kcmil AL- Alcoa Hard Drawn (37) |  | 795 kcmil AL- Alcoa Hard Drawn (37) | 10.0066 | 26.0604 | 90 | 0.071134 | 0.897 | 0.092586
AL- Alcoa Hard Drawn | 874500 | [7 empty] | 37 | 0.1538 |  |  | 1.077 | 14830 | 4334 | 949 | 0.03443 | 0.107 | 0.1075 | 0.1089 | 0.11 | 0.118 | 0.1185 | 0.1198 | 0.121 | 0.1703 | 0.3407 | 0.4088 | 0.221 | 0.1105 | 0.0921 | 0.107 | 0.1047 | 1.077 | 0.03443 | 2 | 0.004308 | 874.5 kcmil AL- Alcoa Hard Drawn (37) |  | 874.5 kcmil AL- Alcoa Hard Drawn (37) | 10.4943 | 27.3558 | 90 | 0.065055 | 0.949 | 0.084672
AL- Alcoa Hard Drawn | 954000 | [7 empty] | 37 | 0.1606 |  |  | 1.024 | 16180 | 4728 | 1000 | 0.03596 | 0.0979 | 0.0985 | 0.1002 | 0.1 | 0.108 | 0.1085 | 0.11 | 0.111 | 0.1682 | 0.3363 | 0.4036 | 0.2179 | 0.109 | 0.0908 | 0.0979 | 0.095791 | 1.024 | 0.03596 | 2 | 0.004308 | 954 kcmil AL- Alcoa Hard Drawn (37) |  | 954 kcmil AL- Alcoa Hard Drawn (37) | 10.9606 | 26.0096 | 90 | 0.059522 | 1 | 0.077471
AL- Alcoa Hard Drawn | 1000000 | [7 empty] | 61 | 0.128 |  |  | 1.152 | 17670 | 4956 | 1030 | 0.03707 | 0.0934 | 0.094 | 0.0956 | 0.0966 | 0.103 | 0.1035 | 0.105 | 0.106 | 0.1666 | 0.3332 | 0.3998 | 0.2162 | 0.1081 | 0.0901 | 0.0934 | 0.091388 | 1.152 | 0.03707 | 2 | 0.004308 | 1000 kcmil AL- Alcoa Hard Drawn (61) |  | 1000 kcmil AL- Alcoa Hard Drawn (61) | 11.2989 | 29.2608 | 90 | 0.056786 | 1.03 | 0.07391
AL- Alcoa Hard Drawn | 1000000 | [7 empty] | 91 | 0.1048 |  |  | 1.153 | 18380 | 4956 | 1030 | 0.0372 | 0.0934 | 0.094 | 0.0956 | 0.0966 | 0.103 | 0.1035 | 0.105 | 0.106 | 0.1664 | 0.3328 | 0.3994 | 0.216 | 0.108 | 0.09 | 0.0934 | 0.091388 | 1.153 | 0.0372 | 2 | 0.004308 | 1000 kcmil AL- Alcoa Hard Drawn (91) |  | 1000 kcmil AL- Alcoa Hard Drawn (91) | 11.3386 | 29.2862 | 90 | 0.056786 | 1.03 | 0.07391
AL- Alcoa Hard Drawn | 1033500 | [7 empty] | 37 | 0.1672 |  |  | 1.17 | 18260 | 5122 | 1050 | 0.03743 | 0.0904 | 0.091 | 0.0927 | 0.0936 | 0.0994 | 0.0999 | 0.1015 | 0.102 | 0.1661 | 0.3322 | 0.3987 | 0.215 | 0.1075 | 0.0895 | 0.0904 | 0.088453 | 1.17 | 0.03743 | 2 | 0.004308 | 1033.5 kcmil AL- Alcoa Hard Drawn (37) |  | 1033.5 kcmil AL- Alcoa Hard Drawn (37) | 11.4087 | 29.718 | 90 | 0.054962 | 1.05 | 0.071536
AL- Alcoa Hard Drawn | 1113000 | [7 empty] | 61 | 0.1351 |  |  | 1.216 | 19660 | 5517 | 1110 | 0.0391 | 0.0839 | 0.0845 | 0.0864 | 0.0874 | 0.0922 | 0.0928 | 0.0945 | 0.0954 | 0.1639 | 0.3278 | 0.3934 | 0.2124 | 0.1062 | 0.0885 | 0.0839 | 0.082093 | 1.216 | 0.0391 | 2 | 0.004308 | 1113 kcmil AL- Alcoa Hard Drawn (61) |  | 1113 kcmil AL- Alcoa Hard Drawn (61) | 11.9177 | 30.8864 | 90 | 0.05101 | 1.11 | 0.066393
AL- Alcoa Hard Drawn | 1192500 | [7 empty] | 61 | 0.1398 |  |  | 1.258 | 21000 | 5908 | 1160 | 0.04048 | 0.0783 | 0.079 | 0.081 | 0.0821 | 0.086 | 0.0866 | 0.0884 | 0.0895 | 0.1622 | 0.3243 | 0.3892 | 0.21 | 0.105 | 0.0875 | 0.0783 | 0.076613 | 1.258 | 0.04048 | 2 | 0.004308 | 1192.5 kcmil AL- Alcoa Hard Drawn (61) |  | 1192.5 kcmil AL- Alcoa Hard Drawn (61) | 12.3383 | 31.9532 | 90 | 0.047605 | 1.16 | 0.061961
AL- Alcoa Hard Drawn | 1192500 | [7 empty] | 91 | 0.1145 |  |  | 1.259 | 21400 | 5908 | 1160 | 0.04062 | 0.0783 | 0.079 | 0.081 | 0.0821 | 0.086 | 0.0866 | 0.0884 | 0.0895 | 0.162 | 0.324 | 0.3888 | 0.2098 | 0.1049 | 0.0874 | 0.0783 | 0.076613 | 1.259 | 0.04062 | 2 | 0.004308 | 1192.5 kcmil AL- Alcoa Hard Drawn (91) |  | 1192.5 kcmil AL- Alcoa Hard Drawn (91) | 12.381 | 31.9786 | 90 | 0.047605 | 1.16 | 0.061961
AL- Alcoa Hard Drawn | 1272000 | [7 empty] | 61 | 0.1444 |  |  | 1.3 | 22000 | 6299 | 1210 | 0.0418 | 0.0734 | 0.0741 | 0.0762 | 0.0774 | 0.0806 | 0.0813 | 0.0832 | 0.0843 | 0.1606 | 0.3211 | 0.3853 | 0.2076 | 0.1038 | 0.0865 | 0.0734 | 0.071819 | 1.3 | 0.0418 | 2 | 0.004308 | 1272 kcmil AL- Alcoa Hard Drawn (61) |  | 1272 kcmil AL- Alcoa Hard Drawn (61) | 12.7406 | 33.02 | 90 | 0.044626 | 1.21 | 0.058084
AL- Alcoa Hard Drawn | 1351500 | [7 empty] | 61 | 0.1489 |  |  | 1.34 | 23400 | 6700 | 1250 | 0.04309 | 0.0691 | 0.0699 | 0.0721 | 0.0733 | 0.076 | 0.0767 | 0.0787 | 0.0798 | 0.159 | 0.318 | 0.3816 | 0.2054 | 0.1027 | 0.0856 | 0.0691 | 0.067612 | 1.34 | 0.04309 | 2 | 0.004308 | 1351.5 kcmil AL- Alcoa Hard Drawn (61) |  | 1351.5 kcmil AL- Alcoa Hard Drawn (61) | 13.1338 | 34.036 | 90 | 0.042012 | 1.25 | 0.054681
AL- Alcoa Hard Drawn | 1431000 | [7 empty] | 61 | 0.1532 |  |  | 1.379 | 24300 | 7091 | 1300 | 0.04434 | 0.0653 | 0.0661 | 0.0685 | 0.0697 | 0.0718 | 0.0725 | 0.0747 | 0.0759 | 0.1576 | 0.3152 | 0.3782 | 0.2033 | 0.1016 | 0.0847 | 0.0653 | 0.063893 | 1.379 | 0.04434 | 2 | 0.004308 | 1431 kcmil AL- Alcoa Hard Drawn (61) |  | 1431 kcmil AL- Alcoa Hard Drawn (61) | 13.5148 | 35.0266 | 90 | 0.039702 | 1.3 | 0.051674
AL- Alcoa Hard Drawn | 1510500 | [7 empty] | 61 | 0.1574 |  |  | 1.417 | 25600 | 7487 | 1320 | 0.04556 | 0.0618 | 0.0627 | 0.0651 | 0.0665 | 0.0679 | 0.0687 | 0.071 | 0.0722 | 0.1562 | 0.3123 | 0.3748 | 0.2014 | 0.1007 | 0.0839 | 0.0618 | 0.060469 | 1.417 | 0.04556 | 2 | 0.004308 | 1510.5 kcmil AL- Alcoa Hard Drawn (61) |  | 1510.5 kcmil AL- Alcoa Hard Drawn (61) | 13.8867 | 35.9918 | 90 | 0.037574 | 1.32 | 0.048904
AL- Alcoa Hard Drawn | 1590000 | [7 empty] | 61 | 0.1615 |  |  | 1.454 | 27000 | 7883 | 1380 | 0.04674 | 0.0597 | 0.0596 | 0.0622 | 0.0636 | 0.0645 | 0.0653 | 0.0677 | 0.069 | 0.1549 | 0.3098 | 0.3718 | 0.1997 | 0.0998 | 0.0832 | 0.0597 | 0.058414 | 1.454 | 0.04674 | 2 | 0.004308 | 1590 kcmil AL- Alcoa Hard Drawn (61) |  | 1590 kcmil AL- Alcoa Hard Drawn (61) | 14.2464 | 36.9316 | 90 | 0.036297 | 1.38 | 0.047242
AL- Alcoa Hard Drawn | 1590000 | [7 empty] | 91 | 0.1322 |  |  | 1.454 | 28100 | 7883 | 1380 | 0.04691 | 0.0587 | 0.0596 | 0.0622 | 0.0636 | 0.0645 | 0.0653 | 0.0677 | 0.069 | 0.1547 | 0.3094 | 0.3713 | 0.1997 | 0.0998 | 0.0832 | 0.0587 | 0.057436 | 1.454 | 0.04691 | 2 | 0.004308 | 1590 kcmil AL- Alcoa Hard Drawn (91) |  | 1590 kcmil AL- Alcoa Hard Drawn (91) | 14.2982 | 36.9316 | 90 | 0.035689 | 1.38 | 0.046451
ACSR | 1590 |  |  | 54 | 3 | 0.1716 | 19 | 0.103 |  |  |  |  | 1.545 | 56000 | 10777 | 1380 | 0.052 | 0.0587 | 0.0588 | 0.059 | 0.0591 | 0.0646 | 0.0656 | 0.0675 | 0.0684 | 0.1495 | 0.299 | 0.359 | 0.1953 | 0.0977 | 0.0814 | 0.0587 | 0.057436 | 1.545 | 0.052 | 1 | 0.004308 | 1.59 kcmil ACSR |  | 1.59 kcmil ACSR | 15.8496 | 39.243 | 95 | 0.035689 | 1.38 | 0.04722
ACSR | 1510500 |  |  | 54 | 3 | 0.1673 | 19 | 0.1004 |  |  |  |  | 1.506 | 53200 | 10237 | 1340 | 0.0507 | 0.0618 | 0.0619 | 0.0621 | 0.0622 | 0.068 | 0.069 | 0.071 | 0.072 | 0.1508 | 0.302 | 0.362 | 0.1971 | 0.0986 | 0.0821 | 0.0618 | 0.060469 | 1.506 | 0.0507 | 1 | 0.004308 | 1510.5 kcmil ACSR |  | 1510.5 kcmil ACSR | 15.4534 | 38.2524 | 95 | 0.037574 | 1.34 | 0.049714
ACSR | 1431000 |  |  | 54 | 3 | 0.1628 | 19 | 0.0977 |  |  |  |  | 1.465 | 50400 | 9699 | 1300 | 0.0493 | 0.0652 | 0.0653 | 0.0655 | 0.0656 | 0.0718 | 0.0729 | 0.0749 | 0.076 | 0.1522 | 0.304 | 0.365 | 0.1991 | 0.0996 | 0.083 | 0.0652 | 0.063796 | 1.465 | 0.0493 | 1 | 0.004308 | 1431 kcmil ACSR |  | 1431 kcmil ACSR | 15.0266 | 37.211 | 95 | 0.039641 | 1.3 | 0.052449
ACSR | 1351000 |  |  | 54 | 3 | 0.1582 | 19 | 0.0949 |  |  |  |  | 1.424 | 47600 | 9160 | 1250 | 0.0479 | 0.0691 | 0.0692 | 0.0694 | 0.0695 | 0.0761 | 0.0771 | 0.0792 | 0.0803 | 0.1536 | 0.307 | 0.369 | 0.201 | 0.1006 | 0.0838 | 0.0691 | 0.067612 | 1.424 | 0.0479 | 1 | 0.004308 | 1351 kcmil ACSR |  | 1351 kcmil ACSR | 14.5999 | 36.1696 | 95 | 0.042012 | 1.25 | 0.055586
ACSR | 1272000 |  |  | 54 | 3 | 0.1535 | 19 | 0.0921 |  |  |  |  | 1.382 | 44800 | 8621 | 1200 | 0.0465 | 0.0734 | 0.0735 | 0.0737 | 0.0738 | 0.0808 | 0.0819 | 0.084 | 0.0851 | 0.1551 | 0.31 | 0.372 | 0.203 | 0.1016 | 0.0847 | 0.0734 | 0.071819 | 1.382 | 0.0465 | 1 | 0.004308 | 1272 kcmil ACSR |  | 1272 kcmil ACSR | 14.1732 | 35.1028 | 95 | 0.044626 | 1.2 | 0.059045
ACSR | 1192500 |  |  | 54 | 3 | 0.1486 | 19 | 0.0892 |  |  |  |  | 1.338 | 43100 | 8082 | 1160 | 0.045 | 0.0783 | 0.0784 | 0.0786 | 0.0788 | 0.0862 | 0.0872 | 0.0894 | 0.0906 | 0.1568 | 0.314 | 0.376 | 0.206 | 0.1028 | 0.0857 | 0.0783 | 0.076613 | 1.338 | 0.045 | 1 | 0.004308 | 1192.5 kcmil ACSR |  | 1192.5 kcmil ACSR | 13.716 | 33.9852 | 95 | 0.047605 | 1.16 | 0.062987
ACSR | 1113000 |  |  | 54 | 3 | 0.1436 | 19 | 0.0862 |  |  |  |  | 1.293 | 40200 | 7544 | 1110 | 0.0435 | 0.0839 | 0.084 | 0.0842 | 0.0844 | 0.0924 | 0.0935 | 0.0957 | 0.0969 | 0.1585 | 0.317 | 0.38 | 0.208 | 0.104 | 0.0867 | 0.0839 | 0.082093 | 1.293 | 0.0435 | 1 | 0.004308 | 1113 kcmil ACSR |  | 1113 kcmil ACSR | 13.2588 | 32.8422 | 95 | 0.05101 | 1.11 | 0.067491
ACSR | 1033500 |  |  | 54 | 3 | 0.1384 | 7 | 0.1384 |  |  |  |  | 1.246 | 37100 | 7019 | 1060 | 0.042 | 0.0903 | 0.0905 | 0.0907 | 0.0908 | 0.0994 | 0.1005 | 0.1025 | 0.1035 | 0.1603 | 0.321 | 0.385 | 0.211 | 0.1053 | 0.0878 | 0.0903 | 0.088355 | 1.246 | 0.042 | 1 | 0.004308 | 1033.5 kcmil ACSR |  | 1033.5 kcmil ACSR | 12.8016 | 31.6484 | 95 | 0.054901 | 1.06 | 0.07264
ACSR | 954000 |  |  | 54 | 3 | 0.1329 | 7 | 0.1329 |  |  |  |  | 1.196 | 34200 | 6479 | 1010 | 0.0403 | 0.0979 | 0.098 | 0.0981 | 0.0982 | 0.1078 | 0.1088 | 0.1118 | 0.1128 | 0.1624 | 0.325 | 0.39 | 0.214 | 0.1068 | 0.089 | 0.0979 | 0.095791 | 1.196 | 0.0403 | 1 | 0.004308 | 954 kcmil ACSR |  | 954 kcmil ACSR | 12.2834 | 30.3784 | 95 | 0.059522 | 1.01 | 0.078753
ACSR | 900000 |  |  | 54 | 3 | 0.1291 | 7 | 0.1291 |  |  |  |  | 1.162 | 32300 | 6112 | 970 | 0.0391 | 0.104 | 0.104 | 0.104 | 0.104 | 0.1145 | 0.1155 | 0.1175 | 0.1185 | 0.1639 | 0.328 | 0.393 | 0.216 | 0.1078 | 0.0898 | 0.104 | 0.10176 | 1.162 | 0.0391 | 1 | 0.004308 | 900 kcmil ACSR |  | 900 kcmil ACSR | 11.9177 | 29.5148 | 95 | 0.063231 | 0.97 | 0.08366
ACSR | 874500 |  |  | 54 | 3 | 0.1273 | 7 | 0.1273 |  |  |  |  | 1.146 | 31400 | 5940 | 950 | 0.0386 | 0.107 | 0.107 | 0.107 | 0.108 | 0.1178 | 0.1188 | 0.1218 | 0.1228 | 0.1646 | 0.329 | 0.395 | 0.217 | 0.1083 | 0.0903 | 0.107 | 0.1047 | 1.146 | 0.0386 | 1 | 0.004308 | 874.5 kcmil ACSR |  | 874.5 kcmil ACSR | 11.7653 | 29.1084 | 95 | 0.065055 | 0.95 | 0.086074
ACSR | 795000 |  |  | 54 | 3 | 0.1214 | 7 | 0.1214 |  |  |  |  | 1.093 | 28500 | 5399 | 900 | 0.0368 | 0.117 | 0.118 | 0.118 | 0.119 | 0.1288 | 0.1308 | 0.1358 | 0.1378 | 0.167 | 0.334 | 0.401 | 0.22 | 0.11 | 0.0917 | 0.117 | 0.11448 | 1.093 | 0.0368 | 1 | 0.004308 | 795 kcmil ACSR | 1 | 795 kcmil ACSR - 1 | 11.2166 | 27.7622 | 95 | 0.071134 | 0.9 | 0.094118
ACSR | 795000 |  |  | 26 | 2 | 0.1749 | 7 | 0.136 |  |  |  |  | 1.108 | 31200 | 5770 | 900 | 0.0375 | 0.117 | 0.117 | 0.117 | 0.117 | 0.1288 | 0.1288 | 0.1288 | 0.1288 | 0.166 | 0.332 | 0.399 | 0.219 | 0.1095 | 0.0912 | 0.117 | 0.11448 | 1.108 | 0.0375 | 1 | 0.004308 | 795 kcmil ACSR | 2 | 795 kcmil ACSR - 2 | 11.43 | 28.1432 | 95 | 0.071134 | 0.9 | 0.094118
ACSR | 795000 |  |  | 30 | 2 | 0.1628 | 19 | 0.0977 |  |  |  |  | 1.14 | 38400 | 6517 | 910 | 0.0393 | 0.117 | 0.117 | 0.117 | 0.117 | 0.1288 | 0.1288 | 0.1288 | 0.1288 | 0.1637 | 0.327 | 0.393 | 0.217 | 0.1085 | 0.0904 | 0.117 | 0.11448 | 1.14 | 0.0393 | 1 | 0.004308 | 795 kcmil ACSR | 3 | 795 kcmil ACSR - 3 | 11.9786 | 28.956 | 95 | 0.071134 | 0.91 | 0.094118
ACSR | 715500 |  |  | 54 | 3 | 0.1151 | 7 | 0.1151 |  |  |  |  | 1.036 | 26300 | 4859 | 830 | 0.0349 | 0.131 | 0.131 | 0.131 | 0.132 | 0.1442 | 0.1452 | 0.1472 | 0.1482 | 0.1697 | 0.339 | 0.407 | 0.224 | 0.1119 | 0.0932 | 0.131 | 0.12818 | 1.036 | 0.0349 | 1 | 0.004308 | 715.5 kcmil ACSR | 1 | 715.5 kcmil ACSR - 1 | 10.6375 | 26.3144 | 95 | 0.079646 | 0.83 | 0.10538
ACSR | 715500 |  |  | 26 | 2 | 0.1659 | 7 | 0.129 |  |  |  |  | 1.051 | 28100 | 5193 | 840 | 0.0355 | 0.131 | 0.131 | 0.I3I | 0.131 | 0.1442 | 0.1442 | 0.1442 | 0.1442 | 0.1687 | 0.337 | 0.405 | 0.223 | 0.1114 | 0.0928 | 0.131 | 0.12818 | 1.051 | 0.0355 | 1 | 0.004308 | 715.5 kcmil ACSR | 2 | 715.5 kcmil ACSR - 2 | 10.8204 | 26.6954 | 95 | 0.079646 | 0.84 | 0.10538
ACSR | 715500 |  |  | 30 | 2 | 0.1544 | 19 | 0.0926 |  |  |  |  | 1.081 | 34600 | 5865 | 840 | 0.0372 | 0.131 | 0.131 | 0.131 | 0.131 | 0.1442 | 0.1442 | 0.1442 | 0.1442 | 0.1664 | 0.333 | 0.399 | 0.221 | 0.1104 | 0.092 | 0.131 | 0.12818 | 1.081 | 0.0372 | 1 | 0.004308 | 715.5 kcmil ACSR | 3 | 715.5 kcmil ACSR - 3 | 11.3386 | 27.4574 | 95 | 0.079646 | 0.84 | 0.10538
ACSR | 666600 |  |  | 54 | 3 | 0.1111 | 7 | 0.1111 |  |  |  |  | 1 | 24500 | 4527 | 800 | 0.0337 | 0.14 | 0.14 | 0.141 | 0.141 | 0.1541 | 0.1571 | 0.1591 | 0.1601 | 0.1715 | 0.343 | 0.412 | 0.226 | 0.1132 | 0.0943 | 0.14 | 0.13698 | 1 | 0.0337 | 1 | 0.004308 | 666.6 kcmil ACSR |  | 666.6 kcmil ACSR | 10.2718 | 25.4 | 95 | 0.085118 | 0.8 | 0.11262
ACSR | 636000 |  |  | 54 | 3 | 0.1085 | 7 | 0.1085 |  |  |  |  | 0.977 | 23600 | 4319 | 770 | 0.0329 | 0.147 | 0.147 | 0.148 | 0.148 | 0.1618 | 0.1638 | 0.1678 | 0.1688 | 0.1726 | 0.345 | 0.414 | 0.228 | 0.114 | 0.095 | 0.147 | 0.14383 | 0.977 | 0.0329 | 1 | 0.004308 | 636 kcmil ACSR |  | 636 kcmil ACSR | 10.0279 | 24.8158 | 95 | 0.089374 | 0.77 | 0.11825
ACSR | 636 |  |  | 26 | 2 | 0.1564 | 7 | 0.1216 |  |  |  |  | 0.99 | 25000 | 4616 | 780 | 0.0335 | 0.147 | 0.147 | 0.147 | 0.147 | 0.1618 | 0.1618 | 0.1618 | 0.1618 | 0.1718 | 0.344 | 0.412 | 0.227 | 0.1135 | 0.0946 | 0.147 | 0.14383 | 0.99 | 0.0335 | 1 | 0.004308 | 0.636 kcmil ACSR | 1 | 0.636 kcmil ACSR - 1 | 10.2108 | 25.146 | 95 | 0.089374 | 0.78 | 0.11825
ACSR | 636 |  |  | 30 | 2 | 0.1456 | 19 | 0.0874 |  |  |  |  | 1.019 | 31500 | 5213 | 780 | 0.0351 | 0.147 | 0.147 | 0.147 | 0.147 | 0.1618 | 0.1618 | 0.1618 | 0.1618 | 0.1693 | 0.339 | 0.406 | 0.225 | 0.1125 | 0.0937 | 0.147 | 0.14383 | 1.019 | 0.0351 | 1 | 0.004308 | 0.636 kcmil ACSR | 2 | 0.636 kcmil ACSR - 2 | 10.6985 | 25.8826 | 95 | 0.089374 | 0.78 | 0.11825
ACSR | 605000 |  |  | 54 | 3 | 0.1059 | 7 | 0.1059 |  |  |  |  | 0.953 | 22500 | 4109 | 750 | 0.0321 | 0.154 | 0.155 | 0.155 | 0.155 | 0.1695 | 0.1715 | 0.1755 | 0.1775 | 0.1739 | 0.348 | 0.417 | 0.23 | 0.1149 | 0.0957 | 0.154 | 0.15068 | 0.953 | 0.0321 | 1 | 0.004308 | 605 kcmil ACSR | 1 | 605 kcmil ACSR - 1 | 9.7841 | 24.2062 | 95 | 0.09363 | 0.75 | 0.12388
ACSR | 605000 |  |  | 26 | 2 | 0.1525 | 7 | 0.1186 |  |  |  |  | 0.966 | 24100 | 4391 | 760 | 0.0327 | 0.154 | 0.154 | 0.154 | 0.154 | 0.17 | 0.172 | 0.172 | 0.172 | 0.173 | 0.346 | 0.415 | 0.229 | 0.1144 | 0.0953 | 0.154 | 0.15068 | 0.966 | 0.0327 | 1 | 0.004308 | 605 kcmil ACSR | 2 | 605 kcmil ACSR - 2 | 9.967 | 24.5364 | 95 | 0.09363 | 0.76 | 0.12388
ACSR | 556500 |  |  | 26 | 2 | 0.1463 | 7 | 0.1138 |  |  |  |  | 0.927 | 22400 | 4039 | 730 | 0.0313 | 0.168 | 0.168 | 0.168 | 0.168 | 0.1849 | 0.1859 | 0.1859 | 0.1859 | 0.1751 | 0.35 | 0.42 | 0.232 | 0.1159 | 0.0965 | 0.168 | 0.16438 | 0.927 | 0.0313 | 1 | 0.004308 | 556.5 kcmil ACSR | 1 | 556.5 kcmil ACSR - 1 | 9.5402 | 23.5458 | 95 | 0.10214 | 0.73 | 0.13514
ACSR | 556500 |  |  | 30 | 2 | 0.1362 | 7 | 0.1362 |  |  |  |  | 0.953 | 27200 | 4588 | 730 | 0.0328 | 0.168 | 0.168 | 0.168 | 0.168 | 0.1849 | 0.1859 | 0.1859 | 0.1859 | 0.1728 | 0.346 | 0.415 | 0.23 | 0.1149 | 0.0957 | 0.168 | 0.16438 | 0.953 | 0.0328 | 1 | 0.004308 | 556.5 kcmil ACSR | 2 | 556.5 kcmil ACSR - 2 | 9.9974 | 24.2062 | 95 | 0.10214 | 0.73 | 0.13514
ACSR | 500000 |  |  | 30 | 2 | 0.1291 | 7 | 0.1291 |  |  |  |  | 0.904 | 24400 | 4122 | 690 | 0.0311 | 0.187 | 0.187 | 0.187 | 0.187 | 0.206 | 0.206 | 0.206 | 0.206 | 0.1754 | 0.351 | 0.421 | 0.234 | 0.1167 | 0.0973 | 0.187 | 0.18297 | 0.904 | 0.0311 | 1 | 0.004308 | 500 kcmil ACSR |  | 500 kcmil ACSR | 9.4793 | 22.9616 | 95 | 0.11369 | 0.69 | 0.15043
ACSR | 477000 |  |  | 26 | 2 | 0.1355 | 7 | 0.1054 |  |  |  |  | 0.858 | 19430 | 3462 | 670 | 0.029 | 0.196 | 0.196 | 0.196 | 0.196 | 0.216 | 0.216 | 0.216 | 0.216 | 0.179 | 0.358 | 0.43 | 0.237 | 0.1186 | 0.0988 | 0.196 | 0.19178 | 0.858 | 0.029 | 1 | 0.004308 | 477 kcmil ACSR | 1 | 477 kcmil ACSR - 1 | 8.8392 | 21.7932 | 95 | 0.11917 | 0.67 | 0.15767
ACSR | 477000 |  |  | 30 | 2 | 0.1261 | 7 | 0.1261 |  |  |  |  | 0.883 | 23300 | 3933 | 670 | 0.0304 | 0.196 | 0.196 | 0.196 | 0.196 | 0.216 | 0.216 | 0.216 | 0.216 | 0.1766 | 0.353 | 0.424 | 0.235 | 0.1176 | 0.098 | 0.196 | 0.19178 | 0.883 | 0.0304 | 1 | 0.004308 | 477 kcmil ACSR | 2 | 477 kcmil ACSR - 2 | 9.2659 | 22.4282 | 95 | 0.11917 | 0.67 | 0.15767
ACSR | 397500 |  |  | 26 | 2 | 0.1236 | 7 | 0.0961 |  |  |  |  | 0.783 | 16190 | 2885 | 590 | 0.0265 | 0.235 | 0.235 | 0.235 | 0.235 | 0.259 | 0.259 | 0.259 | 0.259 | 0.1836 | 0.367 | 0.441 | 0.244 | 0.1219 | 0.1015 | 0.235 | 0.22994 | 0.783 | 0.0265 | 1 | 0.004308 | 397.5 kcmil ACSR | 1 | 397.5 kcmil ACSR - 1 | 8.0772 | 19.8882 | 95 | 0.14288 | 0.59 | 0.18904
ACSR | 397500 |  |  | 30 | 2 | 0.1151 | 7 | 0.1151 |  |  |  |  | 0.806 | 19980 | 3277 | 600 | 0.0278 | 0.235 | 0.235 | 0.235 | 0.235 | 0.259 | 0.259 | 0.259 | 0.259 | 0.1812 | 0.362 | 0.435 | 0.242 | 0.1208 | 0.1006 | 0.235 | 0.22994 | 0.806 | 0.0278 | 1 | 0.004308 | 397.5 kcmil ACSR | 2 | 397.5 kcmil ACSR - 2 | 8.4734 | 20.4724 | 95 | 0.14288 | 0.6 | 0.18904
ACSR | 336400 |  |  | 26 | 2 | 0.1138 | 7 | 0.0885 |  |  |  |  | 0.721 | 14050 | 2442 | 530 | 0.0244 | 0.278 | 0.278 | 0.278 | 0.278 | 0.306 | 0.306 | 0.306 | 0.306 | 0.1872 | 0.376 | 0.451 | 0.25 | 0.1248 | 0.1039 | 0.278 | 0.27201 | 0.721 | 0.0244 | 1 | 0.004308 | 336.4 kcmil ACSR | 1 | 336.4 kcmil ACSR - 1 | 7.4371 | 18.3134 | 95 | 0.16902 | 0.53 | 0.22363
ACSR | 336400 |  |  | 30 | 2 | 0.1059 | 7 | 0.1059 |  |  |  |  | 0.741 | 17040 | 2774 | 530 | 0.0255 | 0.278 | 0.278 | 0.278 | 0.278 | 0.306 | 0.306 | 0.306 | 0.306 | 0.1855 | 0.371 | 0.445 | 0.248 | 0.1238 | 0.1032 | 0.278 | 0.27201 | 0.741 | 0.0255 | 1 | 0.004308 | 336.4 kcmil ACSR | 2 | 336.4 kcmil ACSR - 2 | 7.7724 | 18.8214 | 95 | 0.16902 | 0.53 | 0.22363
ACSR | 300 |  |  | 26 | 2 | 0.1074 | 7 | 0.0835 |  |  |  |  | 0.68 | 12650 | 2178 | 490 | 0.023 | 0.311 | 0.311 | 0.311 | 0.311 | 0.342 | 0.342 | 0.342 | 0.342 | 0.1908 | 0.382 | 0.458 | 0.254 | 0.1269 | 0.1057 | 0.311 | 0.3043 | 0.68 | 0.023 | 1 | 0.004308 | 0.3 kcmil ACSR | 1 | 0.3 kcmil ACSR - 1 | 7.0104 | 17.272 | 95 | 0.18908 | 0.49 | 0.25018
ACSR | 300 |  |  | 30 | 2 | 0.1 | 7 | 0.1 |  |  |  |  | 0.7 | 15430 | 2473 | 500 | 0.0241 | 0.311 | 0.311 | 0.311 | 0.311 | 0.342 | 0.342 | 0.342 | 0.342 | 0.1883 | 0.377 | 0.452 | 0.252 | 0.1258 | 0.1049 | 0.311 | 0.3043 | 0.7 | 0.0241 | 1 | 0.004308 | 0.3 kcmil ACSR | 2 | 0.3 kcmil ACSR - 2 | 7.3457 | 17.78 | 95 | 0.18908 | 0.5 | 0.25018
ACSR | 266.8 |  |  | 26 | 2 | 0.1013 | 7 | 0.0788 |  |  |  |  | 0.642 | 11250 | 1936 | 460 | 0.0217 | 0.35 | 0.35 | 0.35 | 0.35 | 0.385 | 0.385 | 0.385 | 0.385 | 0.1936 | 0.387 | 0.465 | 0.258 | 0.1289 | 0.1074 | 0.35 | 0.34246 | 0.642 | 0.0217 | 1 | 0.004308 | 0.2668 kcmil ACSR |  | 0.2668 kcmil ACSR | 6.6142 | 16.3068 | 95 | 0.2128 | 0.46 | 0.28155
ACSR | 266800 |  |  | 6 | 1 | 0.2109 | 7 | 0.0703 |  |  |  |  | 0.633 | 9645 | 1802 | 460 | 0.00684 | 0.351 | 0.351 | 0.351 | 0.352 | 0.386 | 0.43 | 0.51 | 0.552 | 0.252 | 0.504 | 0.605 | 0.259 | 0.1294 | 0.1079 | 0.351 | 0.34344 | 0.633 | 0.00684 | 1 | 0.004308 | 266.8 kcmil ACSR |  | 266.8 kcmil ACSR | 2.0848 | 16.0782 | 95 | 0.2134 | 0.46 | 0.28235
ACSR | 4/0 | 4/0 |  | 6 | 1 | 0.1878 | 1 | 0.1878 |  |  |  |  | 0.563 | 8420 | 1542 | 340 | 0.00814 | 0.441 | 0.442 | 0.444 | 0.445 | 0.485 | 0.514 | 0.567 | 0.592 | 0.242 | 0.484 | 0.581 | 0.267 | 0.1336 | 0.1113 | 0.441 | 0.4315 | 0.563 | 0.00814 | 1 | 0.004308 | 4/0 ACSR |  | 4/0 ACSR | 2.4811 | 14.3002 | 95 | 0.26812 | 0.34 | 0.35475
ACSR | 3/0 | 3/0 |  | 6 | 1 | 0.1672 | 1 | 0.1672 |  |  |  |  | 0.502 | 6675 | 1223 | 300 | 0.006 | 0.556 | 0.557 | 0.559 | 0.56 | 0.612 | 0.642 | 0.697 | 0.723 | 0.259 | 0.517 | 0.621 | 0.275 | 0.1377 | 0.1147 | 0.556 | 0.54402 | 0.502 | 0.006 | 1 | 0.004308 | 3/0 ACSR |  | 3/0 ACSR | 1.8288 | 12.7508 | 95 | 0.33804 | 0.3 | 0.44726
ACSR | 2/0 | 2/0 |  | 6 | 1 | 0.149 | 1 | 0.149 |  |  |  |  | 0.447 | 5345 | 970 | 270 | 0.0051 | 0.702 | 0.702 | 0.704 | 0.706 | 0.773 | 0.806 | 0.866 | 0.895 | 0.267 | 0.534 | 0.641 | 0.284 | 0.1418 | 0.1182 | 0.702 | 0.68688 | 0.447 | 0.0051 | 1 | 0.004308 | 2/0 ACSR |  | 2/0 ACSR | 1.5545 | 11.3538 | 95 | 0.42681 | 0.27 | 0.56471
ACSR | 1/0 | 1/0 |  | 6 | 1 | 0.1327 | 1 | 0.1327 |  |  |  |  | 0.398 | 4280 | 769 | 230 | 0.00446 | 0.885 | 0.885 | 0.887 | 0.888 | 0.974 | 1.01 | 1.08 | 1.12 | 0.273 | 0.547 | 0.656 | 0.292 | 0.146 | 0.1216 | 0.885 | 0.86594 | 0.398 | 0.00446 | 1 | 0.004308 | 1/0 ACSR |  | 1/0 ACSR | 1.3594 | 10.1092 | 95 | 0.53807 | 0.23 | 0.71192
ACSR | 1 | 1 |  | 6 | 1 | 0.1182 | 1 | 0.1182 |  |  |  |  | 0.355 | 3480 | 610 | 200 | 0.00418 | 1.12 | 1.12 | 1.12 | 1.12 | 1.23 | 1.27 | 1.34 | 1.38 | 0.277 | 0.554 | 0.665 | 0.3 | 0.15 | 0.125 | 1.12 | 1.0959 | 0.355 | 0.00418 | 1 | 0.004308 | 1 ACSR |  | 1 ACSR | 1.2741 | 9.017 | 95 | 0.68095 | 0.2 | 0.90096
ACSR | 2 | 2 |  | 6 | 1 | 0.1052 | 1 | 0.1052 |  |  |  |  | 0.316 | 2790 | 484 | 180 | 0.00418 | 1.41 | 1.41 | 1.41 | 1.41 | 1.55 | 1.59 | 1.66 | 1.69 | 0.277 | 0.554 | 0.665 | 0.308 | 0.1542 | 0.1285 | 1.41 | 1.3796 | 0.316 | 0.00418 | 1 | 0.004308 | 2 ACSR | 1 | 2 ACSR - 1 | 1.2741 | 8.0264 | 95 | 0.85726 | 0.18 | 1.1342
ACSR | 2 | 2 |  | 7 | 1 | 0.0974 | 1 | 0.1299 |  |  |  |  | 0.325 | 3525 | 566 | 180 | 0.00504 | 1.41 | 1.41 | 1.41 | 1.41 | 1.55 | 1.59 | 1.62 | 1.65 | 0.267 | 0.535 | 0.642 | 0.306 | 0.1532 | 0.1276 | 1.41 | 1.3796 | 0.325 | 0.00504 | 1 | 0.004308 | 2 ACSR | 2 | 2 ACSR - 2 | 1.5362 | 8.255 | 95 | 0.85726 | 0.18 | 1.1342
ACSR | 3 | 3 |  | 6 | 1 | 0.0937 | 1 | 0.0937 |  |  |  |  | 0.281 | 2250 | 384 | 160 | 0.0043 | 1.78 | 1.78 | 1.78 | 1.78 | 1.95 | 1.95 | 2.04 | 2.07 | 0.275 | 0.551 | 0.661 | 0.317 | 0.1583 | 0.132 | 1.78 | 1.7417 | 0.281 | 0.0043 | 1 | 0.004308 | 3 ACSR |  | 3 ACSR | 1.3106 | 7.1374 | 95 | 1.0822 | 0.16 | 1.4319
ACSR | 4 | 4 |  | 6 | 1 | 0.0834 | 1 | 0.0834 |  |  |  |  | 0.25 | 1830 | 304 | 140 | 0.00437 | 2.24 | 2.24 | 2.24 | 2.24 | 2.47 | 2.5 | 2.54 | 2.57 | 0.274 | 0.549 | 0.659 | 0.325 | 0.1627 | 0.1355 | 2.24 | 2.1918 | 0.25 | 0.00437 | 1 | 0.004308 | 4 ACSR | 1 | 4 ACSR - 1 | 1.332 | 6.35 | 95 | 1.3619 | 0.14 | 1.8019
ACSR | 4 | 4 |  | 7 | 1 | 0.0772 | 1 | 0.1029 |  |  |  |  | 0.257 | 2288 | 356 | 140 | 0.00452 | 2.24 | 2.24 | 2.24 | 2.24 | 2.47 | 2.5 | 2.53 | 2.55 | 0.273 | 0.545 | 0.655 | 0.323 | 0.1615 | 0.1346 | 2.24 | 2.1918 | 0.257 | 0.00452 | 1 | 0.004308 | 4 ACSR | 2 | 4 ACSR - 2 | 1.3777 | 6.5278 | 95 | 1.3619 | 0.14 | 1.8019
ACSR | 5 | 5 |  | 6 | 1 | 0.0743 | 1 | 0.0743 |  |  |  |  | 0.223 | 1460 | 241 | 120 | 0.00416 | 2.82 | 2.82 | 2.82 | 2.82 | 3.1 | 3.12 | 3.16 | 3.18 | 0.279 | 0.557 | 0.665 | 0.333 | 0.1666 | 0.1388 | 2.82 | 2.7593 | 0.223 | 0.00416 | 1 | 0.004308 | 5 ACSR |  | 5 ACSR | 1.268 | 5.6642 | 95 | 1.7145 | 0.12 | 2.2685
ACSR | 6 | 6 |  | 6 | 1 | 0.0661 | 1 | 0.0661 |  |  |  |  | 0.198 | 1170 | 191 | 100 | 0.00394 | 3.56 | 3.56 | 3.56 | 3.56 | 3.92 | 3.94 | 3.97 | 3.98 | 0.281 | 0.561 | 0.673 | 0.342 | 0.1708 | 0.1423 | 3.56 | 3.4833 | 0.198 | 0.00394 | 1 | 0.004308 | 6 ACSR |  | 6 ACSR | 1.2009 | 5.0292 | 95 | 2.1644 | 0.1 | 2.8638
CU- Copperweld | 350 E |  | 350 E | [9 empty] | 0.788 | 32420 | 7409 | 660 | 0.022 | 0.1658 | 0.1728 | 0.1789 | 0.1812 | 0.1812 | 0.1915 | 0.201 | 0.204 | 0.1929 | 0.386 | 0.463 | 0.243 | 0.1216 | 0.1014 | 0.1658 | 0.16245 | 0.788 | 0.022 | 5 | 0.004041 | 350 E CU- Copperweld |  | 350 E CU- Copperweld | 6.7056 | 20.0152 | 75 | 0.10094 | 0.66 | 0.12338
CU- Copperweld | 350 EK |  | 350 EK | [9 empty] | 0.735 | 23850 | 6536 | 680 | 0.0245 | 0.1658 | 0.1682 | 0.17 | 0.1705 | 0.1812 | 0.1845 | 0.1873 | 0.1882 | 0.1875 | 0.375 | 0.45 | 0.248 | 0.1241 | 0.1034 | 0.1658 | 0.16245 | 0.735 | 0.0245 | 5 | 0.004041 | 350 EK CU- Copperweld |  | 350 EK CU- Copperweld | 7.4676 | 18.669 | 75 | 0.10094 | 0.68 | 0.12338
CU- Copperweld | 350 V |  | 350 V | [9 empty] | 0.754 | 23480 | 6578 | 650 | 0.0226 | 0.1655 | 0.1725 | 0.18 | 0.1828 | 0.1809 | 0.191 | 0.202 | 0.206 | 0.1915 | 0.383 | 0.46 | 0.246 | 0.1232 | 0.1027 | 0.1655 | 0.16216 | 0.754 | 0.0226 | 5 | 0.004041 | 350 V CU- Copperweld |  | 350 V CU- Copperweld | 6.8885 | 19.1516 | 75 | 0.10076 | 0.65 | 0.12315
CU- Copperweld | 300 E |  | 300 E | [9 empty] | 0.729 | 27770 | 6351 | 500 | 0.0204 | 0.1934 | 0.2 | 0.207 | 0.209 | 0.211 | 0.222 | 0.232 | 0.235 | 0.1969 | 0.394 | 0.473 | 0.249 | 0.1244 | 0.1037 | 0.1934 | 0.18949 | 0.729 | 0.0204 | 5 | 0.004041 | 300 E CU- Copperweld |  | 300 E CU- Copperweld | 6.2179 | 18.5166 | 75 | 0.11775 | 0.5 | 0.14391
CU- Copperweld | 300 EK |  | 300 EK | [9 empty] | 0.68 | 20960 | 5602 | 610 | 0.0227 | 0.1934 | 0.1958 | 0.1976 | 0.198 | 0.211 | 0.215 | 0.218 | 0.219 | 0.1914 | 0.383 | 0.46 | 0.254 | 0.1269 | 0.1057 | 0.1934 | 0.18949 | 0.68 | 0.0227 | 5 | 0.004041 | 300 EK CU- Copperweld |  | 300 EK CU- Copperweld | 6.919 | 17.272 | 75 | 0.11775 | 0.61 | 0.14391
CU- Copperweld | 300 V |  | 300 V | [9 empty] | 0.698 | 20730 | 5639 | 590 | 0.0208 | 0.193 | 0.2 | 0.208 | 0.21 | 0.211 | 0.222 | 0.233 | 0.237 | 0.1954 | 0.391 | 0.469 | 0.252 | 0.1259 | 0.105 | 0.193 | 0.1891 | 0.698 | 0.0208 | 5 | 0.004041 | 300 V CU- Copperweld |  | 300 V CU- Copperweld | 6.3398 | 17.7292 | 75 | 0.1175 | 0.59 | 0.14362
CU- Copperweld | 250 E |  | 250 E | [9 empty] | 0.666 | 23920 | 5292 | 540 | 0.01859 | 0.232 | 0.239 | 0.245 | 0.248 | 0.254 | 0.265 | 0.275 | 0.279 | 0.202 | 0.403 | 0.484 | 0.255 | 0.1276 | 0.1604 | 0.232 | 0.22731 | 0.666 | 0.01859 | 5 | 0.004041 | 250 E CU- Copperweld |  | 250 E CU- Copperweld | 5.6662 | 16.9164 | 75 | 0.14125 | 0.54 | 0.17264
CU- Copperweld | 250 EK |  | 250 EK | [9 empty] | 0.621 | 17840 | 4669 | 540 | 0.0207 | 0.232 | 0.235 | 0.236 | 0.237 | 0.254 | 0.258 | 0.261 | 0.261 | 0.196 | 0.392 | 0.471 | 0.26 | 0.1301 | 0.1084 | 0.232 | 0.22731 | 0.621 | 0.0207 | 5 | 0.004041 | 250 EK CU- Copperweld |  | 250 EK CU- Copperweld | 6.3094 | 15.7734 | 75 | 0.14125 | 0.54 | 0.17264
CU- Copperweld | 250 V |  | 250 V | [9 empty] | 0.637 | 17420 | 4699 | 530 | 0.01911 | 0.232 | 0.239 | 0.246 | 0.249 | 0.253 | 0.264 | 0.276 | 0.281 | 0.2 | 0.4 | 0.48 | 0.258 | 0.1292 | 0.1077 | 0.232 | 0.22731 | 0.637 | 0.01911 | 5 | 0.004041 | 250 V CU- Copperweld |  | 250 V CU- Copperweld | 5.8247 | 16.1798 | 75 | 0.14125 | 0.53 | 0.17264
CU- Copperweld | 4/0 E |  | 4/0 E | [9 empty] | 0.613 | 20730 | 4479 | 480 | 0.01711 | 0.274 | 0.281 | 0.287 | 0.29 | 0.3 | 0.312 | 0.323 | 0.326 | 0.206 | 0.411 | 0.493 | 0.261 | 0.1306 | 0.1088 | 0.274 | 0.26846 | 0.613 | 0.01711 | 5 | 0.004041 | 4/0 E CU- Copperweld |  | 4/0 E CU- Copperweld | 5.2151 | 15.5702 | 75 | 0.16682 | 0.48 | 0.20389
CU- Copperweld | 4/0 G |  | 4/0 G | [9 empty] | 0.583 | 1540 | 4168 | 460 | 0.01409 | 0.273 | 0.284 | 0.294 | 0.298 | 0.299 | 0.318 | 0.336 | 0.342 | 0.215 | 0.431 | 0.517 | 0.265 | 0.1324 | 0.1103 | 0.273 | 0.26748 | 0.583 | 0.01409 | 5 | 0.004041 | 4/0 G CU- Copperweld |  | 4/0 G CU- Copperweld | 4.2946 | 14.8082 | 75 | 0.16621 | 0.46 | 0.20315
CU- Copperweld | 4/0 EK |  | 4/0 EK | [9 empty] | 0.571 | 15370 | 3951 | 490 | 0.01903 | 0.274 | 0.277 | 0.278 | 0.279 | 0.3 | 0.304 | 0.307 | 0.308 | 0.2 | 0.401 | 0.481 | 0.266 | 0.1331 | 0.1109 | 0.274 | 0.26846 | 0.571 | 0.01903 | 5 | 0.004041 | 4/0 EK CU- Copperweld |  | 4/0 EK CU- Copperweld | 5.8003 | 14.5034 | 75 | 0.16682 | 0.49 | 0.20389
CU- Copperweld | 4/0 V |  | 4/0 V | [9 empty] | 0.586 | 15000 | 3977 | 470 | 0.01758 | 0.274 | 0.281 | 0.288 | 0.291 | 0.299 | 0.311 | 0.323 | 0.328 | 0.204 | 0.409 | 0.49 | 0.264 | 0.1322 | 0.1101 | 0.274 | 0.26846 | 0.586 | 0.01758 | 5 | 0.004041 | 4/0 V CU- Copperweld |  | 4/0 V CU- Copperweld | 5.3584 | 14.8844 | 75 | 0.16682 | 0.47 | 0.20389
CU- Copperweld | 4/0 F |  | 4/0 F | [9 empty] | 0.55 | 12290 | 3750 | 470 | 0.01558 | 0.273 | 0.28 | 0.285 | 0.287 | 0.299 | 0.309 | 0.318 | 0.322 | 0.21 | 0.421 | 0.505 | 0.269 | 0.1344 | 0.122 | 0.273 | 0.26748 | 0.55 | 0.01558 | 5 | 0.004041 | 4/0 F CU- Copperweld |  | 4/0 F CU- Copperweld | 4.7488 | 13.97 | 75 | 0.16621 | 0.47 | 0.20315
CU- Copperweld | 3/0 E |  | 3/0 E | [9 empty] | 0.545 | 16800 | 3522 | 420 | 0.01521 | 0.346 | 0.353 | 0.359 | 0.361 | 0.378 | 0.391 | 0.402 | 0.407 | 0.212 | 0.423 | 0.608 | 0.27 | 0.1348 | 0.1123 | 0.346 | 0.33901 | 0.545 | 0.01521 | 5 | 0.004041 | 3/0 E CU- Copperweld |  | 3/0 E CU- Copperweld | 4.636 | 13.843 | 75 | 0.21065 | 0.42 | 0.25747
CU- Copperweld | 3/0 J |  | 3/0 J | [9 empty] | 0.555 | 16170 | 3732 | 410 | 0.01158 | 0.344 | 0.356 | 0.367 | 0.372 | 0.377 | 0.398 | 0.419 | 0.428 | 0.225 | 0.451 | 0.541 | 0.268 | 0.1341 | 0.1118 | 0.344 | 0.33705 | 0.555 | 0.01158 | 5 | 0.004041 | 3/0 J CU- Copperweld |  | 3/0 J CU- Copperweld | 3.5296 | 14.097 | 75 | 0.20943 | 0.41 | 0.25598
CU- Copperweld | 310 G |  | 310 G | [9 empty] | 0.519 | 12860 | 3305 | 400 | 0.01254 | 0.344 | 0.355 | 0.365 | 0.369 | 0.377 | 0.397 | 0.416 | 0.423 | 0.221 | 0.443 | 0.531 | 0.273 | 0.1365 | 0.1137 | 0.344 | 0.33705 | 0.519 | 0.01254 | 5 | 0.004041 | 310 G CU- Copperweld |  | 310 G CU- Copperweld | 3.8222 | 13.1826 | 75 | 0.20943 | 0.4 | 0.25598
CU- Copperweld | 3/0 EK |  | 3/0 EK | [9 empty] | 0.509 | 12370 | 3134 | 420 | 0.01697 | 0.346 | 0.348 | 0.35 | 0.351 | 0.378 | 0.382 | 0.386 | 0.386 | 0.206 | 0.412 | 0.495 | 0.274 | 0.1372 | 0.1143 | 0.346 | 0.33901 | 0.509 | 0.01697 | 5 | 0.004041 | 3/0 EK CU- Copperweld |  | 3/0 EK CU- Copperweld | 5.1725 | 12.9286 | 75 | 0.21065 | 0.42 | 0.25747
CU- Copperweld | 3/0 V |  | 3/0 V | [9 empty] | 0.522 | 12220 | 3154 | 410 | 0.01566 | 0.345 | 0.352 | 0.36 | 0.362 | 0.377 | 0.39 | 0.403 | 0.408 | 0.21 | 0.42 | 0.504 | 0.273 | 0.1363 | 0.1136 | 0.345 | 0.33803 | 0.522 | 0.01566 | 5 | 0.004041 | 3/0 V CU- Copperweld |  | 3/0 V CU- Copperweld | 4.7732 | 13.2588 | 75 | 0.21004 | 0.41 | 0.25672
CU- Copperweld | 3/0 F |  | 3/0 F | [9 empty] | 0.49 | 9980 | 2974 | 410 | 0.01388 | 0.344 | 0.351 | 0.366 | 0.358 | 0.377 | 0.388 | 0.397 | 0.401 | 0.216 | 0.432 | 0.519 | 0.277 | 0.1385 | 0.1155 | 0.344 | 0.33705 | 0.49 | 0.01388 | 5 | 0.004041 | 3/0 F CU- Copperweld |  | 3/0 F CU- Copperweld | 4.2306 | 12.446 | 75 | 0.20943 | 0.41 | 0.25598
CU- Copperweld | 2/0 K |  | 2/0 K | [9 empty] | 0.534 | 17600 | 3411 | 360 | 0.00912 | 0.434 | 0.447 | 0.459 | 0.466 | 0.475 | 0.499 | 0.524 | 0.535 | 0.237 | 0.476 | 0.57 | 0.271 | 0.1355 | 0.1129 | 0.434 | 0.42523 | 0.534 | 0.00912 | 5 | 0.004041 | 2/0 K CU- Copperweld |  | 2/0 K CU- Copperweld | 2.7798 | 13.5636 | 75 | 0.26423 | 0.36 | 0.32295
CU- Copperweld | 2/0 J |  | 2/0 J | [9 empty] | 0.494 | 13430 | 2960 | 350 | 0.01029 | 0.434 | 0.446 | 0.457 | 0.462 | 0.475 | 0.498 | 0.52 | 0.53 | 0.231 | 0.463 | 0.555 | 0.277 | 0.1383 | 0.1152 | 0.434 | 0.42523 | 0.494 | 0.01029 | 5 | 0.004041 | 2/0 J CU- Copperweld |  | 2/0 J CU- Copperweld | 3.1364 | 12.5476 | 75 | 0.26423 | 0.35 | 0.32295
CU- Copperweld | 2/0 G |  | 2/0 G | [9 empty] | 0.463 | 10510 | 2622 | 350 | 0.01119 | 0.434 | 0.445 | 0.456 | 0.459 | 0.475 | 0.497 | 0.518 | 0.526 | 0.227 | 0.454 | 0.545 | 0.281 | 0.1406 | 0.1171 | 0.434 | 0.42523 | 0.463 | 0.01119 | 5 | 0.004041 | 2/0 G CU- Copperweld |  | 2/0 G CU- Copperweld | 3.4107 | 11.7602 | 75 | 0.26423 | 0.35 | 0.32295
CU- Copperweld | 2/0 V |  | 2/0 V | [9 empty] | 0.465 | 9846 | 2502 | 360 | 0.01395 | 0.435 | 0.442 | 0.45 | 0.452 | 0.476 | 0.489 | 0.504 | 0.509 | 0.216 | 0.432 | 0.518 | 0.281 | 0.1404 | 0.117 | 0.435 | 0.42621 | 0.465 | 0.01395 | 5 | 0.004041 | 2/0 V CU- Copperweld |  | 2/0 V CU- Copperweld | 4.252 | 11.811 | 75 | 0.26484 | 0.36 | 0.3237
CU- Copperweld | 2/0 F |  | 2/0 F | [9 empty] | 0.436 | 8094 | 2359 | 350 | 0.01235 | 0.434 | 0.441 | 0.446 | 0.448 | 0.475 | 0.487 | 0.497 | 0.501 | 0.222 | 0.444 | 0.533 | 0.285 | 0.1427 | 0.1189 | 0.434 | 0.42523 | 0.436 | 0.01235 | 5 | 0.004041 | 2/0 F CU- Copperweld |  | 2/0 F CU- Copperweld | 3.7643 | 11.0744 | 75 | 0.26423 | 0.35 | 0.32295
CU- Copperweld | 1/0 K |  | 1/0 K | [9 empty] | 0.475 | 14490 | 2703 | 310 | 0.00812 | 0.548 | 0.56 | 0.573 | 0.579 | 0.599 | 0.625 | 0.652 | 0.664 | 0.243 | 0.487 | 0.584 | 0.279 | 0.1397 | 0.1164 | 0.548 | 0.53693 | 0.475 | 0.00812 | 5 | 0.004041 | 1/0 K CU- Copperweld |  | 1/0 K CU- Copperweld | 2.475 | 12.065 | 75 | 0.33363 | 0.31 | 0.40778
CU- Copperweld | 1/0 J |  | 1/0 J | [9 empty] | 0.44 | 10970 | 2346 | 310 | 0.00917 | 0.548 | 0.559 | 0.57 | 0.576 | 0.699 | 0.624 | 0.648 | 0.659 | 0.237 | 0.474 | 0.589 | 0.285 | 0.1423 | 0.1188 | 0.548 | 0.53693 | 0.44 | 0.00917 | 5 | 0.004041 | 1/0 J CU- Copperweld |  | 1/0 J CU- Copperweld | 2.795 | 11.176 | 75 | 0.33363 | 0.31 | 0.40778
CU- Copperweld | 1/0G |  | 1/0G | [9 empty] | 0.412 | 8563 | 2078 | 310 | 0.00995 | 0.548 | 0.559 | 0.568 | 0.573 | 0.699 | 0.623 | 0.645 | 0.654 | 0.233 | 0.466 | 0.559 | 0.289 | 0.1447 | 0.1206 | 0.548 | 0.53693 | 0.412 | 0.00995 | 5 | 0.004041 | 1/0G CU- Copperweld |  | 1/0G CU- Copperweld | 3.0328 | 10.4648 | 75 | 0.33363 | 0.31 | 0.40778
CU- Copperweld | 1/0 F |  | 1/0 F | [9 empty] | 0.388 | 6536 | 1870 | 310 | 0.01099 | 0.548 | 0.554 | 0.559 | 0.562 | 0.599 | 0.612 | 0.622 | 0.627 | 0.228 | 0.456 | 0.547 | 0.294 | 0.1469 | 0.1224 | 0.548 | 0.53693 | 0.388 | 0.01099 | 5 | 0.004041 | 1/0 F CU- Copperweld |  | 1/0 F CU- Copperweld | 3.3498 | 9.8552 | 75 | 0.33363 | 0.31 | 0.40778
CU- Copperweld | 1 N |  | 1 N | [9 empty] | 0.464 | 15410 | 2541 | 280 | 0.00638 | 0.691 | 0.705 | 0.719 | 0.726 | 0.755 | 0.787 | 0.818 | 0.832 | 0.256 | 0.512 | 0.614 | 0.281 | 0.1405 | 0.1171 | 0.691 | 0.67704 | 0.464 | 0.00638 | 5 | 0.004041 | 1 N CU- Copperweld |  | 1 N CU- Copperweld | 1.9446 | 11.7856 | 75 | 0.42069 | 0.28 | 0.51419
CU- Copperweld | 1 K |  | 1 K | [9 empty] | 0.423 | 11900 | 2144 | 270 | 0.00723 | 0.691 | 0.704 | 0.716 | 0.722 | 0.755 | 0.784 | 0.813 | 0.825 | 0.249 | 0.498 | 0.598 | 0.288 | 0.1438 | 0.1198 | 0.691 | 0.67704 | 0.423 | 0.00723 | 5 | 0.004041 | 1 K CU- Copperweld |  | 1 K CU- Copperweld | 2.2037 | 10.7442 | 75 | 0.42069 | 0.27 | 0.51419
CU- Copperweld | 1 J |  | 1 J | [9 empty] | 0.392 | 9000 | 1881 | 270 | 0.00817 | 0.691 | 0.703 | 0.714 | 0.719 | 0.755 | 0.783 | 0.808 | 0.82 | 0.243 | 0.486 | 0.583 | 0.293 | 0.1465 | 0.1221 | 0.691 | 0.67704 | 0.392 | 0.00817 | 5 | 0.004041 | 1 J CU- Copperweld |  | 1 J CU- Copperweld | 2.4902 | 9.9568 | 75 | 0.42069 | 0.27 | 0.51419
CU- Copperweld | 1 G |  | 1 G | [9 empty] | 0.367 | 6956 | 1649 | 260 | 0.00887 | 0.691 | 0.702 | 0.712 | 0.716 | 0.755 | 0.781 | 0.805 | 0.815 | 0.239 | 0.478 | 0.573 | 0.298 | 0.1488 | 0.124 | 0.691 | 0.67704 | 0.367 | 0.00887 | 5 | 0.004041 | 1 G CU- Copperweld |  | 1 G CU- Copperweld | 2.7036 | 9.3218 | 75 | 0.42069 | 0.26 | 0.51419
CU- Copperweld | 1 F |  | 1 F | [9 empty] | 0.346 | 5266 | 1483 | 270 | 0.0098 | 0.691 | 0.698 | 0.704 | 0.705 | 0.755 | 0.769 | 0.781 | 0.786 | 0.234 | 0.468 | 0.561 | 0.302 | 0.1509 | 0.1258 | 0.691 | 0.67704 | 0.346 | 0.0098 | 5 | 0.004041 | 1 F CU- Copperweld |  | 1 F CU- Copperweld | 2.987 | 8.7884 | 75 | 0.42069 | 0.27 | 0.51419
CU- Copperweld | 2 P |  | 2 P | [9 empty] | 0.452 | 16870 | 2487 | 250 | 0.00501 | 0.871 | 0.886 | 0.901 | 0.909 | 0.952 | 0.988 | 1.024 | 1.04 | 0.268 | 0.536 | 0.643 | 0.281 | 0.1406 | 0.1172 | 0.871 | 0.8534 | 0.452 | 0.00501 | 5 | 0.004041 | 2 P CU- Copperweld |  | 2 P CU- Copperweld | 1.527 | 11.4808 | 75 | 0.53028 | 0.25 | 0.64814
CU- Copperweld | 2 N |  | 2 N | [9 empty] | 0.413 | 12880 | 2015 | 240 | 0.00568 | 0.871 | 0.885 | 0.899 | 0.906 | 0.952 | 0.986 | 1.02 | 1.035 | 0.261 | 0.523 | 0.627 | 0.289 | 0.1445 | 0.1208 | 0.871 | 0.8534 | 0.413 | 0.00568 | 5 | 0.004041 | 2 N CU- Copperweld |  | 2 N CU- Copperweld | 1.7313 | 10.4902 | 75 | 0.53028 | 0.24 | 0.64814
CU- Copperweld | 2 K |  | 2 K | [9 empty] | 0.377 | 9730 | 1701 | 240 | 0.00644 | 0.871 | 0.884 | 0.896 | 0.902 | 0.952 | 0.983 | 1.014 | 1.028 | 0.255 | 0.51 | 0.612 | 0.296 | 0.1479 | 0.1232 | 0.871 | 0.8534 | 0.377 | 0.00644 | 5 | 0.004041 | 2 K CU- Copperweld |  | 2 K CU- Copperweld | 1.9629 | 9.5758 | 75 | 0.53028 | 0.24 | 0.64814
CU- Copperweld | 2 J |  | 2 J | [9 empty] | 0.349 | 7322 | 1476 | 230 | 0.00727 | 0.871 | 0.883 | 0.894 | 0.899 | 0.952 | 0.982 | 1.01 | 1.022 | 0.249 | 0.498 | 0.598 | 0.301 | 0.1506 | 0.1255 | 0.871 | 0.8534 | 0.349 | 0.00727 | 5 | 0.004041 | 2 J CU- Copperweld |  | 2 J CU- Copperweld | 2.2159 | 8.8646 | 75 | 0.53028 | 0.23 | 0.64814
CU- Copperweld | 2A |  | 2A | [9 empty] | 0.366 | 5876 | 1356 | 240 | 0.00763 | 0.869 | 0.875 | 0.88 | 0.882 | 0.95 | 0.962 | 0.973 | 0.979 | 0.247 | 0.493 | 0.592 | 0.298 | 0.1489 | 0.1241 | 0.869 | 0.85144 | 0.366 | 0.00763 | 5 | 0.004041 | 2A CU- Copperweld |  | 2A CU- Copperweld | 2.3256 | 9.2964 | 75 | 0.52906 | 0.24 | 0.64665
CU- Copperweld | 2G |  | 2G | [9 empty] | 0.327 | 5626 | 1307 | 230 | 0.0079 | 0.871 | 0.882 | 0.892 | 0.896 | 0.952 | 0.98 | 1.006 | 1.016 | 0.246 | 0.489 | 0.587 | 0.306 | 0.1529 | 0.1276 | 0.871 | 0.8534 | 0.327 | 0.0079 | 5 | 0.004041 | 2G CU- Copperweld |  | 2G CU- Copperweld | 2.4079 | 8.3058 | 75 | 0.53028 | 0.23 | 0.64814
CU- Copperweld | 2F |  | 2F | [9 empty] | 0.308 | 4233 | 1176 | 230 | 0.00873 | 0.871 | 0.878 | 0.884 | 0.885 | 0.952 | 0.967 | 0.979 | 0.986 | 0.23 | 0.479 | 0.576 | 0.31 | 0.1551 | 0.1292 | 0.871 | 0.8534 | 0.308 | 0.00873 | 5 | 0.004041 | 2F CU- Copperweld |  | 2F CU- Copperweld | 2.6609 | 7.8232 | 75 | 0.53028 | 0.23 | 0.64814
CU- Copperweld | 3P |  | 3P | [9 empty] | 0.411 | 13910 | 1973 | 220 | 0.00445 | 1.098 | 1.113 | 1.127 | 1.136 | 1.2 | 1.239 | 1.273 | 1.296 | 0.274 | 0.647 | 0.657 | 0.29 | 0.1448 | 0.1207 | 1.098 | 1.0758 | 0.411 | 0.00445 | 5 | 0.004041 | 3P CU- Copperweld |  | 3P CU- Copperweld | 1.3564 | 10.4394 | 75 | 0.66848 | 0.22 | 0.81705
CU- Copperweld | 3N |  | 3N | [9 empty] | 0.368 | 10390 | 1598 | 210 | 0.00506 | 1.098 | 1.112 | 1.126 | 1.133 | 1.2 | 1.237 | 1.273 | 1.289 | 0.267 | 0.634 | 0.641 | 0.298 | 0.1487 | 0.1239 | 1.098 | 1.0758 | 0.368 | 0.00506 | 5 | 0.004041 | 3N CU- Copperweld |  | 3N CU- Copperweld | 1.5423 | 9.3472 | 75 | 0.66848 | 0.21 | 0.81705
CU- Copperweld | 3 K |  | 3 K | [9 empty] | 0.336 | 7910 | 1349 | 210 | 0.00674 | 1.098 | 1.111 | 1.123 | 1.129 | 1.2 | 1.233 | 1.267 | 1.281 | 0.261 | 0.622 | 0.626 | 0.304 | 0.152 | 0.1266 | 1.098 | 1.0758 | 0.336 | 0.00674 | 5 | 0.004041 | 3 K CU- Copperweld |  | 3 K CU- Copperweld | 2.0544 | 8.5344 | 75 | 0.66848 | 0.21 | 0.81705
CU- Copperweld | 3 J |  | 3 J | [9 empty] | 0.311 | 5956 | 1171 | 200 | 0.00648 | 1.098 | 1.11 | 1.121 | 1.126 | 1.2 | 1.232 | 1.262 | 1.275 | 0.255 | 0.609 | 0.611 | 0.309 | 0.1547 | 0.1289 | 1.098 | 1.0758 | 0.311 | 0.00648 | 5 | 0.004041 | 3 J CU- Copperweld |  | 3 J CU- Copperweld | 1.9751 | 7.8994 | 75 | 0.66848 | 0.2 | 0.81705
CU- Copperweld | 3A |  | 3A | [9 empty] | 0.326 | 4810 | 1075 | 210 | 0.00679 | 1.096 | 1.102 | 1.107 | 1.109 | 1.198 | 1.211 | 1.226 | 1.229 | 0.252 | 0.606 | 0.606 | 0.306 | 0.1531 | 0.1275 | 1.096 | 1.0739 | 0.326 | 0.00679 | 5 | 0.004041 | 3A CU- Copperweld |  | 3A CU- Copperweld | 2.0696 | 8.2804 | 75 | 0.66726 | 0.21 | 0.81557
CU- Copperweld | 4P |  | 4P | [9 empty] | 0.366 | 11420 | 1584 | 190 | 0.00397 | 1.385 | 1.4 | 1.414 | 1.423 | 1.514 | 1.555 | 1.598 | 1.616 | 0.28 | 0.559 | 0.671 | 0.298 | 0.1489 | 0.1241 | 1.385 | 1.357 | 0.366 | 0.00397 | 5 | 0.004041 | 4P CU- Copperweld |  | 4P CU- Copperweld | 1.2101 | 9.2964 | 75 | 0.84321 | 0.19 | 1.0306
CU- Copperweld | 4N |  | 4N | [9 empty] | 0.328 | 8460 | 1267 | 180 | 0.00451 | 1.385 | 1.399 | 1.413 | 1.42 | 1.514 | 1.554 | 1.593 | 1.61 | 0.273 | 0.546 | 0.655 | 0.306 | 0.1528 | 0.1274 | 1.385 | 1.357 | 0.328 | 0.00451 | 5 | 0.004041 | 4N CU- Copperweld |  | 4N CU- Copperweld | 1.3746 | 8.3312 | 75 | 0.84321 | 0.18 | 1.0306
CU- Copperweld | 4D |  | 4D | [9 empty] | 0.348 | 7340 | 1191 | 190 | 0.00586 | 1.382 | 1.389 | 1.396 | 1.399 | 1.511 | 1.529 | 1.544 | 1.542 | 0.262 | 0.523 | 0.628 | 0.301 | 0.1507 | 0.1256 | 1.382 | 1.3541 | 0.348 | 0.00586 | 5 | 0.004041 | 4D CU- Copperweld |  | 4D CU- Copperweld | 1.7861 | 8.8392 | 75 | 0.84138 | 0.19 | 1.0284
CU- Copperweld | 4A |  | 4A | [9 empty] | 0.29 | 3938 | 853 | 180 | 0.00604 | 1.382 | 1.388 | 1.393 | 1.395 | 1.511 | 1.525 | 1.54 | 1.545 | 0.258 | 0.517 | 0.62 | 0.316 | 0.1572 | 0.131 | 1.382 | 1.3541 | 0.29 | 0.00604 | 5 | 0.004041 | 4A CU- Copperweld |  | 4A CU- Copperweld | 1.841 | 7.366 | 75 | 0.84138 | 0.18 | 1.0284
CU- Copperweld | 5P |  | 5P | [9 empty] | 0.326 | 9311 | 1240 | 160 | 0.00353 | 1.747 | 1.762 | 1.776 | 1.785 | 1.909 | 1.954 | 2 | 2.02 | 0.285 | 0.571 | 0.685 | 0.306 | 0.1531 | 0.1275 | 1.747 | 1.7117 | 0.326 | 0.00353 | 5 | 0.004041 | 5P CU- Copperweld |  | 5P CU- Copperweld | 1.0759 | 8.2804 | 75 | 1.0636 | 0.16 | 1.3
CU- Copperweld | 5D |  | 5D | [9 empty] | 0.31 | 6035 | 944 | 160 | 0.00504 | 1.742 | 1.749 | 1.756 | 1.759 | 1.905 | 1.924 | 1.941 | 1.939 | 0.268 | 0.535 | 0.642 | 0.31 | 0.1548 | 0.129 | 1.742 | 1.7068 | 0.31 | 0.00504 | 5 | 0.004041 | 5D CU- Copperweld |  | 5D CU- Copperweld | 1.5362 | 7.874 | 75 | 1.0606 | 0.16 | 1.2963
CU- Copperweld | 5A |  | 5A | [9 empty] | 0.258 | 3193 | 675 | 160 | 0.00538 | 1.742 | 1.748 | 1.753 | 1.755 | 1.905 | 1.92 | 1.938 | 1.941 | 0.264 | 0.528 | 0.634 | 0.323 | 0.1514 | 0.1245 | 1.742 | 1.7068 | 0.258 | 0.00538 | 5 | 0.004041 | 5A CU- Copperweld |  | 5A CU- Copperweld | 1.6398 | 6.5532 | 75 | 1.0606 | 0.16 | 1.2963
CU- Copperweld | 6D |  | 6D | [9 empty] | 0.276 | 4942 | 749 | 140 | 0.00449 | 2.2 | 2.21 | 2.21 | 2.22 | 2.4 | 2.42 | 2.44 | 2.44 | 0.273 | 0.547 | 0.555 | 0.318 | 0.159 | 0.1325 | 2.2 | 2.1555 | 0.276 | 0.00449 | 5 | 0.004041 | 6D CU- Copperweld |  | 6D CU- Copperweld | 1.3686 | 7.0104 | 75 | 1.3394 | 0.14 | 1.6371
CU- Copperweld | 6A |  | 6A | [9 empty] | 0.23 | 2585 | 536 | 140 | 0.00479 | 2.2 | 2.2 | 2.21 | 2.21 | 2.4 | 2.42 | 2.44 | 2.44 | 0.27 | 0.54 | 0.648 | 0.331 | 0.1655 | 0.1379 | 2.2 | 2.1555 | 0.23 | 0.00479 | 5 | 0.004041 | 6A CU- Copperweld |  | 6A CU- Copperweld | 1.46 | 5.842 | 75 | 1.3394 | 0.14 | 1.6371
CU- Copperweld | 6C |  | 6C | [9 empty] | 0.225 | 2143 | 514 | 130 | 0.00469 | 2.2 | 2.2 | 2.21 | 2.21 | 2.4 | 2.42 | 2.44 | 2.44 | 0.271 | 0.542 | 0.651 | 0.333 | 0.1663 | 0.1384 | 2.2 | 2.1555 | 0.225 | 0.00469 | 5 | 0.004041 | 6C CU- Copperweld |  | 6C CU- Copperweld | 1.4295 | 5.715 | 75 | 1.3394 | 0.13 | 1.6371
CU- Copperweld | 7 D |  | 7 D | [9 empty] | 0.246 | 4022 | 594 | 120 | 0.004 | 2.77 | 2.78 | 2.79 | 2.79 | 3.03 | 3.06 | 3.07 | 3.07 | 0.279 | 0.558 | 0.67 | 0.326 | 0.1831 | 0.1359 | 2.77 | 2.714 | 0.246 | 0.004 | 5 | 0.004041 | 7 D CU- Copperweld |  | 7 D CU- Copperweld | 1.2192 | 6.2484 | 75 | 1.6864 | 0.12 | 2.0612
CU- Copperweld | 7 A |  | 7 A | [9 empty] | 0.223 | 2754 | 495 | 120 | 0.00441 | 2.77 | 2.78 | 2.78 | 2.78 | 3.03 | 3.06 | 3.07 | 3.07 | 0.274 | 0.548 | 0.658 | 0.333 | 0.1665 | 0.1388 | 2.77 | 2.714 | 0.223 | 0.00441 | 5 | 0.004041 | 7 A CU- Copperweld |  | 7 A CU- Copperweld | 1.3442 | 5.6642 | 75 | 1.6864 | 0.12 | 2.0612
CU- Copperweld | 8D |  | 8D | [9 empty] | 0.219 | 3256 | 471 | 110 | 0.00356 | 3.49 | 3.5 | 3.51 | 3.51 | 3.82 | 3.84 | 3.86 | 3.86 | 0.285 | 0.57 | 0.684 | 0.334 | 0.1872 | 0.1392 | 3.49 | 3.4195 | 0.219 | 0.00356 | 5 | 0.004041 | 8D CU- Copperweld |  | 8D CU- Copperweld | 1.0851 | 5.5626 | 75 | 2.1248 | 0.11 | 2.597
CU- Copperweld | 8A |  | 8A | [9 empty] | 0.199 | 2233 | 392 | 100 | 0.00394 | 3.49 | 3.5 | 3.51 | 3.51 | 3.82 | 3.84 | 3.86 | 3.87 | 0.28 | 0.56 | 0.672 | 0.341 | 0.1706 | 0.1422 | 3.49 | 3.4195 | 0.199 | 0.00394 | 5 | 0.004041 | 8A CU- Copperweld |  | 8A CU- Copperweld | 1.2009 | 5.0546 | 75 | 2.1248 | 0.1 | 2.597
CU- Copperweld | 8C |  | 8C | [9 empty] | 0.179 | 1362 | 320 | 100 | 0.00373 | 3.49 | 3.5 | 3.51 | 3.51 | 3.82 | 3.84 | 3.86 | 3.86 | 0.283 | 0.565 | 0.679 | 0.349 | 0.1744 | 0.1453 | 3.49 | 3.4195 | 0.179 | 0.00373 | 5 | 0.004041 | 8C CU- Copperweld |  | 8C CU- Copperweld | 1.1369 | 4.5466 | 75 | 2.1248 | 0.1 | 2.597
CU- Copperweld | 9 1/2 D |  | 9 1/2 D | [9 empty] | 0.174 | 1743 | 298 | 85 | 0.00283 | 4.91 | 4.92 | 4.92 | 4.93 | 5.37 | 5.39 | 5.42 | 5.42 | 0.297 | 0.593 | 0.712 | 0.351 | 0.1754 | 0.1462 | 4.91 | 4.8108 | 0.174 | 0.00283 | 5 | 0.004041 | 9 1/2 D CU- Copperweld |  | 9 1/2 D CU- Copperweld | 0.86258 | 4.4196 | 75 | 2.9893 | 0.085 | 3.6537
AL- Alumoweld Strand OH Ground Wire | 7 NO. 5 |  | 7 NO. 5 | [13 empty] | 0.002958 | 1.217 |  |  | 1.24 | [10 empty] | 1.217 | 1.1908 | 0 | 0.002958 | 3 | 0.004308 | 7 NO. 5 AL- Alumoweld Strand OH Ground Wire |  | 7 NO. 5 AL- Alumoweld Strand OH Ground Wire | 0.9016 | 0 | 90 | 0.73992 | 0 | 0.96305
AL- Alumoweld Strand OH Ground Wire | 7 NO. 6 |  | 7 NO. 6 | [13 empty] | 0.002633 | 1.507 |  |  | 1.536 | [10 empty] | 1.507 | 1.4745 | 0 | 0.002633 | 3 | 0.004308 | 7 NO. 6 AL- Alumoweld Strand OH Ground Wire |  | 7 NO. 6 AL- Alumoweld Strand OH Ground Wire | 0.80254 | 0 | 90 | 0.91624 | 0 | 1.1925
AL- Alumoweld Strand OH Ground Wire | 7 NO. 7 |  | 7 NO. 7 | [13 empty] | 0.002345 | 1.9 |  |  | 1.937 | [10 empty] | 1.9 | 1.8591 | 0 | 0.002345 | 3 | 0.004308 | 7 NO. 7 AL- Alumoweld Strand OH Ground Wire |  | 7 NO. 7 AL- Alumoweld Strand OH Ground Wire | 0.71476 | 0 | 90 | 1.1552 | 0 | 1.5035
AL- Alumoweld Strand OH Ground Wire | 7 NO. 8 |  | 7 NO. 8 | [13 empty] | 0.002085 | 2.4 |  |  | 2.44 | [10 empty] | 2.4 | 2.3483 | 0 | 0.002085 | 3 | 0.004308 | 7 NO. 8 AL- Alumoweld Strand OH Ground Wire |  | 7 NO. 8 AL- Alumoweld Strand OH Ground Wire | 0.63551 | 0 | 90 | 1.4592 | 0 | 1.8992
AL- Alumoweld Strand OH Ground Wire | 7 NO. 9 |  | 7 NO. 9 | [13 empty] | 0.001858 | 3.02 |  |  | 3.08 | [10 empty] | 3.02 | 2.9549 | 0 | 0.001858 | 3 | 0.004308 | 7 NO. 9 AL- Alumoweld Strand OH Ground Wire |  | 7 NO. 9 AL- Alumoweld Strand OH Ground Wire | 0.56632 | 0 | 90 | 1.8361 | 0 | 2.3898
AL- Alumoweld Strand OH Ground Wire | 7 NO. 10 |  | 7 NO. 10 | [13 empty] | 0.001658 | 3.81 |  |  | 3.88 | [10 empty] | 3.81 | 3.7279 | 0 | 0.001658 | 3 | 0.004308 | 7 NO. 10 AL- Alumoweld Strand OH Ground Wire |  | 7 NO. 10 AL- Alumoweld Strand OH Ground Wire | 0.50536 | 0 | 90 | 2.3164 | 0 | 3.015
AL- Alumoweld Strand OH Ground Wire | 3 NO. 5 |  | 3 NO. 5 | [13 empty] | 0.00294 | 2.78 |  |  | 2.78 | [10 empty] | 2.78 | 2.7201 | 0 | 0.00294 | 3 | 0.004308 | 3 NO. 5 AL- Alumoweld Strand OH Ground Wire |  | 3 NO. 5 AL- Alumoweld Strand OH Ground Wire | 0.89611 | 0 | 90 | 1.6902 | 0 | 2.1999
AL- Alumoweld Strand OH Ground Wire | 3 NO. 6 |  | 3 NO. 6 | [13 empty] | 0.002618 | 3.51 |  |  | 3.51 | [10 empty] | 3.51 | 3.4344 | 0 | 0.002618 | 3 | 0.004308 | 3 NO. 6 AL- Alumoweld Strand OH Ground Wire |  | 3 NO. 6 AL- Alumoweld Strand OH Ground Wire | 0.79797 | 0 | 90 | 2.134 | 0 | 2.7776
AL- Alumoweld Strand OH Ground Wire | 3 NO. 7 |  | 3 NO. 7 | [13 empty] | 0.002333 | 4.42 |  |  | 4.42 | [10 empty] | 4.42 | 4.3248 | 0 | 0.002333 | 3 | 0.004308 | 3 NO. 7 AL- Alumoweld Strand OH Ground Wire |  | 3 NO. 7 AL- Alumoweld Strand OH Ground Wire | 0.7111 | 0 | 90 | 2.6873 | 0 | 3.4977
AL- Alumoweld Strand OH Ground Wire | 3 NO. 8 |  | 3 NO. 8 | [13 empty] | 0.002078 | 5.58 |  |  | 5.58 | [10 empty] | 5.58 | 5.4598 | 0 | 0.002078 | 3 | 0.004308 | 3 NO. 8 AL- Alumoweld Strand OH Ground Wire |  | 3 NO. 8 AL- Alumoweld Strand OH Ground Wire | 0.63337 | 0 | 90 | 3.3926 | 0 | 4.4156
AL- Alumoweld Strand OH Ground Wire | 3 NO. 9 |  | 3 NO. 9 | [13 empty] | 0.001853 | 7.04 |  |  | 7.04 | [10 empty] | 7.04 | 6.8884 | 0 | 0.001853 | 3 | 0.004308 | 3 NO. 9 AL- Alumoweld Strand OH Ground Wire |  | 3 NO. 9 AL- Alumoweld Strand OH Ground Wire | 0.56479 | 0 | 90 | 4.2802 | 0 | 5.571
AL- Alumoweld Strand OH Ground Wire | 3 NO. 10 |  | 3 NO. 10 | [13 empty] | 0.00165 | 8.87 |  |  | 8.87 | [10 empty] | 8.87 | 8.6789 | 0 | 0.00165 | 3 | 0.004308 | 3 NO. 10 AL- Alumoweld Strand OH Ground Wire |  | 3 NO. 10 AL- Alumoweld Strand OH Ground Wire | 0.50292 | 0 | 90 | 5.3928 | 0 | 7.0191

## RateKit SI
RateKit SI Database
Conductor_SI | Rac@25C | Rac@75C | Alum | OD | CDR_Type | Strand_Ratio | Diam-Outer | UTS | Area | Std-OL | Weight | Diam-Inner | b | m
LARK/AW | 0.1362 | 0.1629 | 201.16 | 20.472 | 1 | 30/7 | 2.9235 | 87 | 248.3221 | 18 | 870.4 | 2.9235 | 1 | 0
GRACKLE | 0.0496 | 0.0588 | 604.24 | 33.985 | 1 | 54/19 | 3.7744 | 186 | 680.6438 | 24 | 2281.3 | 2.2657 | 1 | 0
KINGBIRD | 0.0913 | 0.1087 | 322.26 | 23.876 | 1 | 18/1 | 4.7752 | 70 | 340.3219 | 12 | 1028 | 4.7752 | 1 | 0
KINGBIRD/AW | 0.0903 | 0.1078 | 322.26 | 23.876 | 1 | 18/1 | 4.7752 | 67 | 340.3219 | 12 | 1006.7 | 4.7752 | 1 | 0
KINGFISHER | 0.0278 | 9999 | 1208.48 | 46.228 | 1 | 72/7 | 4.6228 | 242 | 1260.6426 | 27 | 3772.5 | 3.081 | 1 | 0
KINGFISHER/AW | 0.0273 | 9999 | 1208.48 | 46.228 | 1 | 72/7 | 4.6228 | 240 | 1260.6426 | 27 | 3683.2 | 3.081 | 1 | 0
KINGLET/T2 | 0.053 | 0.0628 | 563.96 | 36.957 | 1 | 20/7 | 4.2342 | 136 | 602.1923 | 13 | 1864.1 | 1.8821 | 1 | 0
KIWI | 0.0301 | 0.0349 | 1098.02 | 44.069 | 1 | 72/7 | 4.4069 | 222 | 1145.6751 | 27 | 3427.2 | 2.9388 | 1 | 0
KIWI/AW | 0.0299 | 0.0347 | 1098.02 | 44.069 | 1 | 72/7 | 4.4069 | 219 | 1145.6751 | 27 | 3370.7 | 2.9388 | 1 | 0
KIWI/SD | 0.0301 | 9999 | 1098.02 | 43.815 | 1 | 72/7 | 4.8692 | 226 | 1145.6751 | 24 | 3416.8 | 2.9388 | 1 | 0
LAPWING | 0.0385 | 0.0453 | 805.65 | 38.202 | 1 | 45/7 | 4.7752 | 188 | 861.2886 | 21 | 2666.8 | 3.1826 | 1 | 0
LAPWING/AW | 0.0381 | 0.0448 | 805.65 | 38.202 | 1 | 45/7 | 4.7752 | 185 | 861.2886 | 21 | 2601.3 | 3.1826 | 1 | 0
LAPWING/SD | 0.0385 | 9999 | 805.65 | 37.287 | 1 | 45/7 | 4.6609 | 189 | 861.2886 | 21 | 2665.3 | 3.1826 | 1 | 0
KETTLE/TW | 0.0606 | 0.0725 | 485.01 | 26.924 | 1 | 32/7 | 4.3942 | 116 | 518.5796 | 14 | 1605.7 | 2.4714 | 1 | 0
LARK | 0.1423 | 0.1703 | 201.41 | 20.472 | 1 | 30/7 | 2.9235 | 90 | 248.3221 | 18 | 926.7 | 2.9235 | 1 | 0
JUNCO | 0.2125 | 9999 | 135.19 | 16.764 | 1 | 30/7 | 2.3952 | 61 | 167.0319 | 18 | 622.1 | 2.3952 | 1 | 0
LEGHORN | 0.4045 | 0.6214 | 68.2 | 13.437 | 1 | 12/7 | 2.6899 | 60 | 107.9998 | 12 | 499.9 | 2.6899 | 1 | 0
LEMON | 0.1681 | 0.166 | 207 | 21.006 | 1 | 30/7 | 2.9997 | 90 | 261.4833 | 18 | 973 | 2.9997 | 1 | 0
LIME | 0.1222 | 0.122 | 281.99 | 24.511 | 1 | 30/7 | 3.5001 | 121 | 355.9993 | 18 | 1320 | 3.5001 | 1 | 0
LINNET | 0.1696 | 0.2032 | 170.45 | 18.288 | 1 | 26/7 | 2.888 | 63 | 198.0641 | 16 | 688.4 | 2.2454 | 1 | 0
LINNET/AW | 0.1643 | 0.1965 | 170.45 | 18.288 | 1 | 26/7 | 2.888 | 60 | 198.0641 | 16 | 655.2 | 2.2454 | 1 | 0
LINNET/SD | 0.1696 | 9999 | 170.45 | 18.186 | 1 | 26/7 | 3.0328 | 64 | 198.1932 | 16 | 688.1 | 2.2454 | 1 | 0
LINNET/T2 | 0.0843 | 0.1004 | 340.91 | 29.972 | 1 | 26/7 | 2.888 | 125 | 396.3863 | 16 | 1376.5 | 2.2454 | 1 | 0
MACAW/SD | 0.0743 | 9999 | 402.83 | 25.375 | 1 | 42/7 | 5.4864 | 88 | 423.5475 | 11 | 1273.9 | 1.9406 | 1 | 0
MACKENZIE/TW | 0.0434 | 0.0515 | 688.96 | 31.979 | 1 | 36/7 | 4.9352 | 164 | 736.6437 | 16 | 2276.9 | 2.9439 | 1 | 0
MALLARD | 0.0721 | 0.0857 | 402.83 | 28.956 | 1 | 30/19 | 4.1351 | 171 | 494.7732 | 18 | 1837.9 | 2.4816 | 1 | 0
MALLARD/AW | 0.0688 | 0.082 | 402.83 | 28.956 | 1 | 30/19 | 4.1351 | 165 | 494.7732 | 18 | 1727.8 | 2.4816 | 1 | 0
MANGO | 0.0912 | 0.0951 | 372.99 | 27 | 1 | 54/7 | 2.9997 | 118 | 431.2249 | 24 | 1440 | 2.9997 | 1 | 0
MARTIN | 0.0441 | 0.0522 | 684.81 | 36.17 | 1 | 54/19 | 4.0183 | 206 | 771.6114 | 24 | 2584.9 | 2.4105 | 1 | 0
LAPWING/TW | 0.0377 | 0.0446 | 805.65 | 34.493 | 1 | 36/7 | 5.3391 | 188 | 861.3531 | 16 | 2665.3 | 3.1826 | 1 | 0
HAWK/SD | 0.1199 | 9999 | 241.7 | 21.844 | 1 | 26/7 | 3.7998 | 87 | 281.0317 | 13 | 975.9 | 2.6746 | 1 | 0
PELICAN/T2 | 0.0615 | 0.0729 | 483.39 | 33.858 | 1 | 18/1 | 4.1351 | 105 | 510.1925 | 12 | 1541.3 | 4.1351 | 1 | 0
GRACKLE/SD | 0.0496 | 9999 | 604.24 | 32.36 | 1 | 54/19 | 5.4305 | 186 | 680.6438 | 16 | 2270.9 | 2.2657 | 1 | 0
GRACKLE/TW | 0.0487 | 0.058 | 604.24 | 31.115 | 1 | 38/19 | 4.4983 | 186 | 680.9019 | 16 | 2276.9 | 2.2657 | 1 | 0
GRAPE | 0.2423 | 0.239 | 144 | 17.501 | 1 | 30/7 | 2.4994 | 64 | 181.6125 | 18 | 675 | 2.4994 | 1 | 0
GREBE | 0.0816 | 9999 | 362.54 | 25.629 | 1 | 45/7 | 3.2029 | 92 | 387.9992 | 21 | 1200.9 | 2.1361 | 1 | 0
GROSBEAK | 0.0901 | 0.1075 | 322.26 | 25.146 | 1 | 26/7 | 3.9726 | 112 | 374.7089 | 16 | 1302.4 | 3.0886 | 1 | 0
GROSBEAK/AW | 0.0874 | 0.1043 | 322.26 | 25.146 | 1 | 26/7 | 3.9726 | 110 | 374.7089 | 16 | 1239.6 | 3.0886 | 1 | 0
GROSBEAK/SD | 0.0901 | 9999 | 322.26 | 24.765 | 1 | 26/7 | 4.3764 | 113 | 374.7089 | 13 | 1300.7 | 3.0886 | 1 | 0
GROSBEAK/TW | 0.0886 | 0.1063 | 322.26 | 23.063 | 1 | 20/7 | 4.5288 | 113 | 374.7089 | 12 | 1299.9 | 3.0886 | 1 | 0
GROUSE | 0.6922 | 0.8575 | 40.54 | 9.322 | 1 | 8/1 | 2.54 | 23 | 54.6451 | 8 | 221.7 | 4.2418 | 1 | 0
GUINEA | 0.343 | 0.5425 | 80.57 | 14.63 | 1 | 12/7 | 2.9235 | 71 | 127.5481 | 12 | 590.7 | 2.9235 | 1 | 0
GULL | 0.0864 | 9999 | 337.77 | 25.4 | 1 | 54/7 | 2.8219 | 109 | 381.9992 | 24 | 1276.8 | 2.8219 | 1 | 0
KILLDEER/SD | 0.0922 | 9999 | 322.26 | 23.292 | 1 | 45/7 | 4.6685 | 79 | 344.58 | 19 | 1064 | 2.0142 | 1 | 0
HAWK/AW | 0.1161 | 0.1388 | 241.7 | 21.793 | 1 | 26/7 | 3.4392 | 85 | 280.9027 | 16 | 929.4 | 2.6746 | 1 | 0
MARTIN/TW | 0.0431 | 0.0513 | 684.81 | 33.02 | 1 | 39/19 | 4.7295 | 208 | 771.5468 | 17 | 2580.5 | 2.4105 | 1 | 0
HAWK/T2 | 0.0601 | 0.0713 | 483.39 | 35.687 | 1 | 26/7 | 3.4392 | 173 | 562.0634 | 16 | 1952.3 | 2.6746 | 1 | 0
HAWK/TW | 0.1167 | 0.1415 | 241.7 | 20.041 | 1 | 18/7 | 4.1351 | 86 | 281.0317 | 10 | 974.7 | 2.6746 | 1 | 0
HEN | 0.1187 | 0.1423 | 241.7 | 22.428 | 1 | 30/7 | 3.2029 | 106 | 298.1284 | 18 | 1112.3 | 3.2029 | 1 | 0
HEN/AW | 0.1136 | 0.1358 | 241.7 | 22.428 | 1 | 30/7 | 3.2029 | 104 | 298.1284 | 18 | 1044.7 | 3.2029 | 1 | 0
HEN/T2 | 0.0594 | 0.0708 | 483.39 | 36.703 | 1 | 30/7 | 3.2029 | 212 | 402.5798 | 18 | 2223.6 | 3.2029 | 1 | 0
HUDSON/TW | 0.0493 | 0.0589 | 586.96 | 30.378 | 1 | 26/7 | 5.3619 | 176 | 663.289 | 16 | 2215.9 | 3.7262 | 1 | 0
IBIS | 0.1435 | 0.1721 | 201.41 | 19.888 | 1 | 26/7 | 3.1394 | 73 | 233.9995 | 16 | 813.4 | 2.4409 | 1 | 0
IBIS/AW | 0.1391 | 0.1664 | 201.16 | 19.888 | 1 | 26/7 | 3.1394 | 70 | 233.9995 | 16 | 774.3 | 2.4409 | 1 | 0
IBIS/T2 | 0.0717 | 0.0852 | 402.83 | 32.563 | 1 | 26/7 | 3.1394 | 145 | 467.741 | 16 | 1626.6 | 2.4409 | 1 | 0
JAEGER/T2 | 0.1234 | 0.1381 | 231.26 | 23.419 | 1 | 18/1 | 2.86 | 54 | 244.1285 | 12 | 737.2 | 2.86 | 1 | 0
JAMES/TW | 0.0344 | 0.0406 | 876.9 | 37.338 | 1 | 34/19 | 5.7302 | 264 | 987.998 | 14 | 3305.2 | 2.7305 | 1 | 0
JOREE | 0.0266 | 0.0305 | 1274.35 | 47.752 | 1 | 76/19 | 4.6203 | 274 | 1343.6102 | 28 | 4091 | 2.1565 | 1 | 0
JOREE/AW | 0.0263 | 0.0304 | 1274.35 | 47.752 | 1 | 76/19 | 4.6203 | 270 | 1343.6102 | 28 | 4007.6 | 2.1565 | 1 | 0
HAWK | 0.1199 | 0.1435 | 241.7 | 21.793 | 1 | 26/7 | 3.4392 | 87 | 280.9027 | 16 | 976.2 | 2.6746 | 1 | 0
PARROT/AW | 0.0388 | 0.0458 | 765.37 | 38.227 | 1 | 54/19 | 4.2469 | 225 | 861.9338 | 24 | 2771 | 2.5476 | 1 | 0
OSPREY/AW | 0.103 | 0.123 | 281.98 | 22.327 | 1 | 18/1 | 4.4653 | 59 | 297.5478 | 12 | 880.4 | 4.4653 | 1 | 0
OSPREY/T2 | 0.0532 | 0.0629 | 563.96 | 36.551 | 1 | 18/1 | 4.4653 | 122 | 595.3536 | 12 | 1797.3 | 4.4653 | 1 | 0
OSTRICH | 0.1901 | 0.2274 | 152.01 | 17.272 | 1 | 26/7 | 2.728 | 56 | 177.0319 | 16 | 614.6 | 2.1209 | 1 | 0
OSTRICH/AW | 0.184 | 0.2202 | 152.01 | 17.272 | 1 | 26/7 | 2.728 | 54 | 177.0319 | 16 | 584.7 | 2.1209 | 1 | 0
OSWEGO/TW | 0.0848 | 0.1016 | 336.85 | 23.546 | 1 | 20/7 | 4.6304 | 118 | 391.7412 | 12 | 1359.3 | 3.1598 | 1 | 0
OXBIRD/SD | 0.0508 | 9999 | 604.24 | 32.156 | 1 | 42/7 | 4.0183 | 131 | 635.3536 | 21 | 1913.8 | 2.3774 | 1 | 0
OXBIRD/TW | 0.0493 | 0.0587 | 604.24 | 29.642 | 1 | 30/7 | 5.0648 | 131 | 635.3536 | 14 | 1913.8 | 2.3774 | 1 | 0
PANTHER | 0.1694 | 0.168 | 206.5 | 20.98 | 1 | 30/7 | 2.9997 | 89 | 261.0317 | 18 | 973.9 | 2.9997 | 1 | 0
PARAKEET | 0.1031 | 0.1237 | 281.98 | 23.216 | 1 | 24/7 | 3.8684 | 88 | 318.58 | 15 | 1066.9 | 2.5781 | 1 | 0
PARAKEET/AW | 0.1007 | 0.1203 | 281.98 | 23.216 | 1 | 24/7 | 3.8684 | 86 | 318.58 | 15 | 1023.1 | 2.5781 | 1 | 0
PARAKEET/SD | 0.1031 | 9999 | 281.98 | 22.885 | 1 | 24/7 | 4.1199 | 89 | 318.58 | 13 | 1065.5 | 2.5781 | 1 | 0
PARAKEET/T2 | 0.0523 | 0.0618 | 563.96 | 37.998 | 1 | 24/7 | 3.8684 | 176 | 637.031 | 24 | 2134 | 2.5781 | 1 | 0
MARTIN/AW | 0.0431 | 0.051 | 684.55 | 36.17 | 1 | 54/19 | 4.0183 | 206 | 771.6114 | 24 | 2480.8 | 2.4105 | 1 | 0
PARROT | 0.0398 | 0.047 | 765.37 | 38.227 | 1 | 54/19 | 4.2469 | 230 | 861.9338 | 24 | 2887 | 2.5476 | 1 | 0
ORTOLAN/SD | 0.0573 | 9999 | 523.67 | 29.083 | 1 | 45/7 | 5.5042 | 125 | 559.8698 | 14 | 1727.8 | 2.5654 | 1 | 0
PARSNIP | 0.067 | 0.0717 | 507.99 | 31.496 | 1 | 54/7 | 3.5001 | 153 | 586.9021 | 24 | 1960 | 3.5001 | 1 | 0
PARTRIDGE | 0.2138 | 0.2554 | 135.19 | 16.307 | 1 | 26/7 | 2.573 | 50 | 157.161 | 16 | 546.6 | 2.0015 | 1 | 0
PARTRIDGE/AW | 0.2068 | 0.2474 | 135.19 | 16.307 | 1 | 26/7 | 2.573 | 48 | 157.161 | 16 | 520.3 | 2.0015 | 1 | 0
PARTRIDGE/SD | 0.2138 | 9999 | 135.19 | 16.383 | 1 | 26/7 | 3.1902 | 50 | 157.161 | 12 | 546.2 | 2.0015 | 1 | 0
PARTRIDGE/T2 | 0.106 | 0.1263 | 270.38 | 26.695 | 1 | 26/7 | 2.573 | 101 | 314.1929 | 16 | 1092.3 | 2.0015 | 1 | 0
PAWPAW | 0.0583 | 0.063 | 582.99 | 33.807 | 1 | 54/19 | 3.749 | 179 | 671.6761 | 24 | 2250 | 2.2504 | 1 | 0
PEACH | 0.0365 | 0.0414 | 935.98 | 42.799 | 1 | 54/19 | 4.7498 | 284 | 1077.9978 | 24 | 3600 | 2.8499 | 1 | 0
PEACOCK | 0.0951 | 0.1137 | 306.55 | 24.206 | 1 | 24/7 | 4.0335 | 96 | 346.4509 | 15 | 1160.3 | 2.6899 | 1 | 0
PEACOCK/AW | 0.0928 | 0.1108 | 306.55 | 24.206 | 1 | 24/7 | 4.0335 | 93 | 346.4509 | 15 | 1112.7 | 2.6899 | 1 | 0
PECOS/TW | 0.0364 | 0.0429 | 821.87 | 36.17 | 1 | 39/19 | 5.1791 | 256 | 930.9014 | 17 | 3135.6 | 2.7026 | 1 | 0
PEE DEE/TW | 0.0344 | 0.0406 | 891.08 | 36.246 | 1 | 37/7 | 4.9962 | 208 | 952.9013 | 17 | 2949.5 | 3.3503 | 1 | 0
PELICAN | 0.1212 | 0.1448 | 241.7 | 20.676 | 1 | 18/1 | 4.1351 | 52 | 255.1608 | 12 | 770.9 | 4.1351 | 1 | 0
PELICAN/AW | 0.1191 | 0.1425 | 241.7 | 20.676 | 1 | 18/1 | 4.1351 | 51 | 255.1608 | 12 | 754.8 | 4.1351 | 1 | 0
PARAKEET/TW | 0.1015 | 0.1217 | 281.98 | 21.209 | 1 | 18/7 | 4.4653 | 89 | 318.5155 | 10 | 1063.9 | 2.5781 | 1 | 0
MYSTIC/TW | 0.0849 | 0.1018 | 337.77 | 23.19 | 1 | 20/7 | 4.638 | 107 | 381.5476 | 12 | 1274.3 | 2.8219 | 1 | 0
GOOSE | 0.0907 | 9999 | 322.26 | 24.816 | 1 | 54/7 | 2.7559 | 105 | 363.9993 | 24 | 1218.8 | 2.7559 | 1 | 0
MAUMEE/TW | 0.0739 | 0.0885 | 389.25 | 24.816 | 1 | 20/7 | 4.9784 | 123 | 439.9346 | 12 | 1470 | 3.0353 | 1 | 0
MERGANSER | 0.06 | 9999 | 483.39 | 31.699 | 1 | 30/7 | 4.5339 | 205 | 595.9988 | 18 | 2221.8 | 4.5339 | 1 | 0
MERLIN | 0.1715 | 0.2051 | 170.45 | 17.374 | 1 | 18/1 | 3.4722 | 39 | 179.9351 | 12 | 543.5 | 3.4722 | 1 | 0
MERLIN/AW | 0.1694 | 0.2026 | 170.45 | 17.374 | 1 | 18/1 | 3.4722 | 38 | 179.9351 | 12 | 532.2 | 3.4722 | 1 | 0
MERLIN/T2 | 0.086 | 0.1025 | 340.81 | 28.448 | 1 | 18/1 | 3.4722 | 77 | 359.8702 | 12 | 1086.8 | 3.4722 | 1 | 0
MERLIN/TW | 0.1687 | 9999 | 170.45 | 16.002 | 1 | 14/1 | 3.937 | 38 | 179.8706 | 9 | 543.2 | 3.4722 | 1 | 0
MERRIMACK/TW | 0.0409 | 0.0486 | 726.41 | 34.036 | 1 | 39/19 | 4.8692 | 221 | 817.8693 | 17 | 2738.2 | 2.4841 | 1 | 0
MILLET | 0.1237 | 0.122 | 281.99 | 24.511 | 1 | 30/7 | 3.5001 | 116 | 355.9993 | 18 | 1320 | 3.5001 | 1 | 0
MINK | 0.5589 | 0.636 | 62.2 | 10.973 | 1 | 6/1 | 3.6601 | 22 | 73.5482 | 6 | 254.5 | 3.6601 | 1 | 0
MINORCA | 0.489 | 0.7326 | 56.14 | 12.192 | 1 | 12/7 | 2.4409 | 50 | 88.903 | 12 | 411.6 | 2.4409 | 1 | 0
MIRAMICHI/TW | 0.0409 | 0.0485 | 737.4 | 33.071 | 1 | 36/7 | 5.1079 | 174 | 788.5146 | 16 | 2440.6 | 3.048 | 1 | 0
MOHAWK/TW | 0.0988 | 0.1185 | 289.68 | 21.488 | 1 | 18/7 | 4.5263 | 92 | 327.3542 | 10 | 1093.4 | 2.6162 | 1 | 0
OSPREY | 0.1044 | 0.1243 | 281.98 | 22.327 | 1 | 18/1 | 4.4653 | 61 | 297.5478 | 12 | 899 | 4.4653 | 1 | 0
OLIVE | 0.067 | 0.0717 | 507.99 | 31.496 | 1 | 54/7 | 3.5001 | 159 | 586.9021 | 24 | 1960 | 3.5001 | 1 | 0
MARTIN/SD | 0.0441 | 9999 | 684.81 | 35.992 | 1 | 54/19 | 4.5009 | 208 | 771.6114 | 21 | 2579 | 2.4105 | 1 | 0
ORTOLAN/AW | 0.0565 | 0.067 | 523.67 | 30.785 | 1 | 45/7 | 3.8481 | 121 | 559.5473 | 21 | 1689.1 | 2.5654 | 1 | 0
ORTOLAN | 0.0573 | 0.0684 | 523.67 | 30.785 | 1 | 45/7 | 3.8481 | 123 | 559.5473 | 21 | 1732.2 | 2.5654 | 1 | 0
ORIOLE/AW | 0.1608 | 0.1923 | 170.45 | 18.821 | 1 | 30/7 | 2.6899 | 77 | 210.2576 | 18 | 736.8 | 2.6899 | 1 | 0
ORIOLE | 0.1684 | 0.2013 | 170.45 | 18.821 | 1 | 30/7 | 2.6899 | 77 | 210.2576 | 18 | 784.4 | 2.6899 | 1 | 0
MONONGAHELA/TW | 0.1403 | 0.1683 | 205.26 | 17.297 | 1 | 14/1 | 4.3205 | 45 | 216.9028 | 9 | 656.3 | 3.8608 | 1 | 0
ONION | 0.0777 | 0.0821 | 437.99 | 29.312 | 1 | 54/7 | 3.2512 | 132 | 505.999 | 24 | 1690 | 3.2512 | 1 | 0
MOOSE | 0.0659 | 0.0691 | 515.79 | 31.775 | 1 | 54/7 | 3.5306 | 160 | 579.0311 | 24 | 2001.4 | 3.5306 | 1 | 0
OATS | 0.0912 | 0.0951 | 372.99 | 27 | 1 | 54/7 | 2.9997 | 115 | 431.2249 | 24 | 1440 | 2.9997 | 1 | 0
NUTHATCH/AW | 0.0398 | 0.0469 | 765.37 | 37.211 | 1 | 45/7 | 4.6533 | 177 | 818.0629 | 21 | 2470.3 | 3.1013 | 1 | 0
NUTHATCH | 0.0403 | 0.0475 | 765.37 | 37.211 | 1 | 45/7 | 4.6533 | 178 | 818.0629 | 21 | 2534.3 | 3.1013 | 1 | 0
NELSON/TW | 0.0468 | 0.0556 | 636.97 | 30.81 | 1 | 35/7 | 4.8133 | 152 | 681.0954 | 16 | 2108.7 | 2.8321 | 1 | 0
NECHAKO/TW | 0.0754 | 0.0902 | 389.6 | 23.622 | 1 | 27/1 | 4.2875 | 73 | 401.2895 | 13 | 1163.6 | 3.8608 | 1 | 0
ORTOLAN/TW | 0.0563 | 0.0672 | 523.67 | 27.991 | 1 | 32/7 | 4.5644 | 125 | 559.5473 | 14 | 1733.7 | 2.5654 | 1 | 0
ORANGE | 0.0777 | 0.0821 | 437.99 | 29.312 | 1 | 54/7 | 3.2512 | 137 | 505.999 | 24 | 1690 | 3.2512 | 1 | 0
CARDINAL/TW | 0.0598 | 0.0715 | 483.39 | 27.534 | 1 | 20/7 | 5.5474 | 149 | 546.0634 | 12 | 1824.5 | 3.3757 | 1 | 0
GRACKLE/AW | 0.0484 | 0.0574 | 604.24 | 33.985 | 1 | 54/19 | 3.7744 | 179 | 680.6438 | 24 | 2189.1 | 2.2657 | 1 | 0
BUNTING | 0.05 | 0.0593 | 604.24 | 33.071 | 1 | 45/7 | 4.1351 | 142 | 645.8052 | 21 | 2000.1 | 2.7559 | 1 | 0
BUNTING/AW | 0.0494 | 0.0585 | 604.24 | 33.071 | 1 | 45/7 | 4.1351 | 139 | 645.8052 | 21 | 1951 | 2.7559 | 1 | 0
BUNTING/SD | 0.05 | 9999 | 604.24 | 32.614 | 1 | 45/7 | 4.0742 | 144 | 645.9987 | 21 | 1998.6 | 2.7559 | 1 | 0
BUNTING/TW | 0.0492 | 0.0585 | 604.24 | 29.997 | 1 | 33/7 | 4.8285 | 144 | 645.9987 | 15 | 1998.6 | 2.7559 | 1 | 0
BUTEO | 0.0795 | 9999 | 362.54 | 27.457 | 1 | 30/7 | 3.9218 | 153 | 447.0314 | 18 | 1665.3 | 3.9218 | 1 | 0
CABBAGE | 0.533 | 0.587 | 65.2 | 11.303 | 1 | 6/1 | 3.749 | 21 | 77.2902 | 6 | 268 | 3.749 | 1 | 0
CALUMET/TW | 0.0996 | 0.1195 | 286.44 | 21.793 | 1 | 18/7 | 4.5009 | 102 | 333.2251 | 10 | 1063.7 | 2.9134 | 1 | 0
CAMEL | 0.0732 | 0.0769 | 465.29 | 30.175 | 1 | 54/7 | 3.3503 | 145 | 538.5796 | 24 | 1804.9 | 3.3503 | 1 | 0
CANARY | 0.0646 | 0.077 | 456.03 | 29.515 | 1 | 54/7 | 3.2791 | 142 | 515.0957 | 24 | 1724.8 | 3.2791 | 1 | 0
CANARY/AW | 0.063 | 0.075 | 456.03 | 29.515 | 1 | 54/7 | 3.2791 | 138 | 515.0957 | 24 | 1653.3 | 4.5491 | 1 | 0
CARDINAL | 0.0611 | 0.0727 | 483.39 | 30.378 | 1 | 54/7 | 3.3757 | 150 | 545.9344 | 24 | 1828.9 | 3.3757 | 1 | 0
BRANT/AW | 0.1406 | 0.1681 | 201.41 | 19.609 | 1 | 24/7 | 3.269 | 63 | 227.5479 | 15 | 730.7 | 2.1793 | 1 | 0
CARDINAL/SD | 0.0611 | 9999 | 483.39 | 29.134 | 1 | 54/7 | 5.3899 | 149 | 546.0634 | 13 | 1826 | 3.3757 | 1 | 0
BRANT | 0.1446 | 9999 | 201.41 | 19.609 | 1 | 24/7 | 3.269 | 65 | 227.5479 | 15 | 762.1 | 2.1793 | 1 | 0
CARROT | 0.3336 | 0.372 | 105 | 14.3 | 1 | 6/7 | 4.7498 | 32 | 120.3869 | 6 | 404 | 1.6002 | 1 | 0
CATAWBA/TW | 0.0464 | 0.0552 | 644.52 | 30.556 | 1 | 30/7 | 5.2299 | 140 | 677.7406 | 14 | 2041.8 | 2.4562 | 1 | 0
CHERRY | 0.3336 | 0.372 | 105 | 14.3 | 1 | 6/7 | 4.7498 | 33 | 120.3869 | 6 | 404 | 1.6002 | 1 | 0
CHEYENNE/TW | 0.0503 | 0.0598 | 591.88 | 29.337 | 1 | 30/7 | 5.0114 | 129 | 622.3213 | 14 | 1875.1 | 2.352 | 1 | 0
CHICKADEE | 0.1454 | 0.1734 | 201.41 | 18.872 | 1 | 18/1 | 3.7744 | 44 | 212.5802 | 12 | 642.3 | 3.7744 | 1 | 0
CHICKADEE/AW | 0.1435 | 0.1716 | 201.16 | 18.872 | 1 | 18/1 | 3.7744 | 44 | 212.5802 | 12 | 628.9 | 3.7744 | 1 | 0
CHICKADEE/T2 | 0.0732 | 0.0871 | 402.83 | 30.886 | 1 | 18/1 | 3.7744 | 89 | 425.1604 | 12 | 1284.3 | 3.7744 | 1 | 0
CHUKAR | 0.0349 | 0.0409 | 902.43 | 40.691 | 1 | 84/19 | 3.6982 | 227 | 976.1271 | 30 | 3087.9 | 2.22 | 1 | 0
CHUKAR/AW | 0.0344 | 0.0403 | 902.43 | 40.691 | 1 | 84/19 | 3.6982 | 221 | 976.1271 | 30 | 2998.6 | 2.22 | 1 | 0
CHUKAR/SD | 0.0349 | 9999 | 901.93 | 39.751 | 1 | 84/19 | 4.9708 | 227 | 976.1271 | 21 | 3077.5 | 2.22 | 1 | 0
CHUKAR/TW | 0.0339 | 0.04 | 901.93 | 36.703 | 1 | 37/19 | 5.5702 | 226 | 975.4819 | 17 | 3070.1 | 2.22 | 1 | 0
COCHIN | 0.2597 | 0.43 | 107.07 | 16.866 | 1 | 12/7 | 3.3706 | 92 | 169.548 | 12 | 785 | 3.3706 | 1 | 0
COLUMBIA/TW | 0.059 | 0.0706 | 489.57 | 27.737 | 1 | 21/7 | 5.4483 | 151 | 553.0957 | 13 | 1846.8 | 3.3985 | 1 | 0
CARDINAL/AW | 0.0596 | 0.0709 | 483.39 | 30.378 | 1 | 54/7 | 3.5128 | 146 | 545.9344 | 24 | 1753.1 | 3.3757 | 1 | 0
BLUEBIRD | 0.0296 | 0.0345 | 1092.45 | 44.755 | 1 | 84/19 | 4.0691 | 268 | 1181.2234 | 30 | 3736.8 | 2.4409 | 1 | 0
ALMOND | 1.2002 | 1.267 | 29 | 7.493 | 1 | 6/1 | 2.4994 | 10 | 34.387 | 6 | 119.1 | 2.4994 | 1 | 0
APPLE | 0.8267 | 0.893 | 41.8 | 8.992 | 1 | 6/1 | 2.9997 | 15 | 49.4838 | 6 | 171 | 2.9997 | 1 | 0
ATHABASKA/TW | 0.0314 | 0.037 | 987.86 | 38.202 | 1 | 42/7 | 5.4737 | 231 | 1056.5785 | 18 | 3272.5 | 3.5357 | 1 | 0
AVOCET/TW | 0.0526 | 0.0627 | 563.96 | 28.677 | 1 | 30/7 | 4.892 | 122 | 592.9666 | 14 | 1787.3 | 2.2962 | 1 | 0
BALDPATE | 0.0636 | 9999 | 456.03 | 30.785 | 1 | 30/7 | 4.3993 | 193 | 561.9989 | 18 | 2098.3 | 4.3993 | 1 | 0
BANANA | 0.533 | 0.587 | 65.1 | 11.303 | 1 | 6/1 | 3.749 | 23 | 77.2902 | 6 | 268 | 3.749 | 1 | 0
BARLEY | 1.2002 | 1.267 | 29 | 7.493 | 1 | 6/1 | 2.4994 | 10 | 34.387 | 6 | 119.1 | 2.4994 | 1 | 0
BEAN | 0.8334 | 0.893 | 41.8 | 8.992 | 1 | 6/1 | 2.9997 | 15 | 49.4838 | 6 | 171 | 2.9997 | 1 | 0
BEAR | 0.1348 | 0.137 | 258.49 | 23.47 | 1 | 30/7 | 3.3503 | 111 | 326.6445 | 18 | 1218.5 | 3.3503 | 1 | 0
BISON | 0.0916 | 0.0975 | 371.79 | 26.975 | 1 | 54/7 | 2.9997 | 117 | 430.3862 | 24 | 1442.9 | 2.9997 | 1 | 0
BITTERN | 0.0472 | 0.0558 | 644.52 | 34.163 | 1 | 45/7 | 4.2697 | 152 | 689.0309 | 21 | 2134 | 2.8473 | 1 | 0
BITTERN/AW | 0.0465 | 0.0551 | 644.52 | 34.163 | 1 | 45/7 | 4.2697 | 149 | 689.0309 | 21 | 2080.4 | 2.8473 | 1 | 0
BROLGA | 0.0764 | 0.0798 | 445.09 | 29.515 | 1 | 54/7 | 3.2791 | 138 | 515.1603 | 24 | 1726.1 | 3.2791 | 1 | 0
BITTERN/TW | 0.0463 | 0.055 | 644.52 | 30.988 | 1 | 35/7 | 4.8412 | 154 | 689.0954 | 16 | 2132.5 | 2.8473 | 1 | 0
CONDOR/SD | 0.0727 | 9999 | 402.83 | 26.797 | 1 | 54/7 | 5.1257 | 125 | 455.0313 | 12 | 1522.4 | 3.081 | 1 | 0
BLUEBIRD/AW | 0.0293 | 0.0341 | 1092.45 | 44.755 | 1 | 84/19 | 4.0691 | 262 | 1181.2234 | 30 | 3629.6 | 2.4409 | 1 | 0
BLUEBIRD/SD | 0.0296 | 9999 | 1092.45 | 43.586 | 1 | 84/19 | 5.4483 | 270 | 1181.3525 | 21 | 3726.4 | 2.4409 | 1 | 0
BLUEBIRD/TW | 0.0289 | 0.0338 | 1092.45 | 40.843 | 1 | 64/19 | 4.6634 | 272 | 1181.9976 | 22 | 3742.7 | 2.4409 | 1 | 0
BLUEJAY | 0.0534 | 0.0634 | 563.96 | 31.953 | 1 | 45/7 | 3.9954 | 133 | 603.2246 | 21 | 1867.6 | 2.6645 | 1 | 0
BLUEJAY/AW | 0.0527 | 0.0625 | 563.96 | 31.953 | 1 | 45/7 | 3.9954 | 130 | 603.2246 | 21 | 1821.5 | 2.6645 | 1 | 0
BLUEJAY/SD | 0.0534 | 9999 | 563.96 | 31.572 | 1 | 45/7 | 3.9446 | 135 | 603.2246 | 21 | 1866.2 | 2.6645 | 1 | 0
BLUEJAY/T2 | 0.0267 | 9999 | 1127.91 | 52.299 | 1 | 45/7 | 3.9954 | 265 | 1206.4492 | 45 | 3735.3 | 2.6645 | 1 | 0
BLUEJAY/TW | 0.0525 | 0.0624 | 563.96 | 29.032 | 1 | 33/7 | 4.6634 | 135 | 603.0311 | 15 | 1870.6 | 2.6645 | 1 | 0
BOBOLINK | 0.0423 | 0.05 | 725.09 | 36.246 | 1 | 45/7 | 4.5288 | 170 | 774.8372 | 21 | 2400.4 | 3.0201 | 1 | 0
BOBOLINK/AW | 0.0418 | 0.0493 | 725.09 | 36.246 | 1 | 45/7 | 4.5288 | 167 | 774.8372 | 21 | 2339.4 | 3.0201 | 1 | 0
BOBOLINK/SD | 0.0423 | 9999 | 725.09 | 35.509 | 1 | 45/7 | 4.4374 | 173 | 775.4823 | 21 | 2398.9 | 3.0201 | 1 | 0
BOBOLINK/TW | 0.0415 | 0.0492 | 725.09 | 32.791 | 1 | 36/7 | 5.0648 | 173 | 775.2888 | 16 | 2400.4 | 3.0201 | 1 | 0
BRAHMA | 0.2591 | 0.4424 | 102.96 | 18.136 | 1 | 16/19 | 2.8626 | 126 | 194.8383 | 16 | 1007.3 | 2.4816 | 1 | 0
BITTERN/SD | 0.0472 | 9999 | 644.52 | 33.604 | 1 | 45/7 | 4.1986 | 154 | 689.0309 | 21 | 2132.5 | 2.8473 | 1 | 0
FLICKER | 0.1205 | 0.1442 | 241.7 | 21.488 | 1 | 24/7 | 3.5814 | 77 | 273.0962 | 15 | 914.6 | 2.3876 | 1 | 0
EAGLE | 0.1019 | 0.1218 | 281.98 | 24.206 | 1 | 30/7 | 3.4595 | 124 | 347.8058 | 18 | 1297.5 | 3.4595 | 1 | 0
EAGLE/AW | 0.0976 | 0.1165 | 281.98 | 24.206 | 1 | 30/7 | 3.4595 | 119 | 347.8058 | 18 | 1218.8 | 3.4595 | 1 | 0
EGRET | 0.0895 | 0.1069 | 322.26 | 25.883 | 1 | 30/19 | 3.6982 | 140 | 395.8057 | 18 | 1470.6 | 2.22 | 1 | 0
EGRET/AW | 0.0856 | 0.1023 | 322.26 | 25.883 | 1 | 30/19 | 3.6982 | 133 | 395.8057 | 18 | 1382.4 | 2.22 | 1 | 0
FALCON | 0.038 | 0.0448 | 805.65 | 39.243 | 1 | 54/19 | 4.3586 | 242 | 907.7401 | 24 | 3041.8 | 2.667 | 1 | 0
FALCON/AW | 0.0371 | 0.0437 | 805.65 | 39.243 | 1 | 54/19 | 4.3586 | 236 | 907.7401 | 24 | 2919.8 | 2.667 | 1 | 0
FALCON/SD | 0.038 | 9999 | 805.65 | 38.633 | 1 | 54/19 | 4.2926 | 245 | 907.7401 | 24 | 3034.4 | 2.667 | 1 | 0
FALCON/TW | 0.0372 | 0.0441 | 805.65 | 35.763 | 1 | 42/19 | 4.9428 | 245 | 907.8046 | 18 | 3035.8 | 2.6162 | 1 | 0
FINCH | 0.0529 | 0.0628 | 563.96 | 32.842 | 1 | 54/19 | 3.6474 | 174 | 635.7407 | 24 | 2129.6 | 2.1895 | 1 | 0
FINCH/AW | 0.0516 | 0.0613 | 564.46 | 32.842 | 1 | 54/19 | 3.6474 | 167 | 635.7407 | 24 | 2044.7 | 2.1895 | 1 | 0
FINCH/SD | 0.0529 | 9999 | 563.96 | 31.318 | 1 | 54/19 | 5.4178 | 174 | 635.4826 | 15 | 2119.1 | 2.1895 | 1 | 0
FINCH/TW | 0.052 | 0.062 | 563.96 | 30.099 | 1 | 38/19 | 4.4983 | 174 | 635.5471 | 16 | 2126.6 | 2.1895 | 1 | 0
CONDOR | 0.0727 | 0.087 | 402.83 | 27.737 | 1 | 54/7 | 3.081 | 125 | 454.7733 | 24 | 1523.9 | 3.081 | 1 | 0
FLAMINGO/AW | 0.0843 | 0.1007 | 337.97 | 25.4 | 1 | 24/7 | 4.2342 | 103 | 381.7412 | 15 | 1225.8 | 2.8219 | 1 | 0
DRAKE/SD | 0.0727 | 9999 | 402.83 | 27.356 | 1 | 26/7 | 4.892 | 141 | 468.4507 | 13 | 1626.6 | 3.4544 | 1 | 0
FLICKER/AW | 0.1173 | 0.1402 | 241.7 | 21.488 | 1 | 24/7 | 3.5814 | 74 | 273.0962 | 15 | 877.1 | 2.3876 | 1 | 0
FLICKER/SD | 0.1205 | 9999 | 241.7 | 21.412 | 1 | 24/7 | 3.8151 | 77 | 273.0962 | 13 | 913 | 2.3876 | 1 | 0
FLICKER/T2 | 0.6046 | 0.0718 | 483.39 | 33.147 | 1 | 24/7 | 3.5814 | 153 | 546.0634 | 15 | 1828.9 | 2.3876 | 1 | 0
FLICKER/TW | 0.1183 | 0.1419 | 241.7 | 19.71 | 1 | 18/7 | 4.1351 | 77 | 273.0962 | 10 | 911.9 | 2.3876 | 1 | 0
FLYCATCHER/T2 | 0.057 | 0.0676 | 523.67 | 35.23 | 1 | 18/1 | 4.3028 | 113 | 552.515 | 12 | 1668.8 | 4.3028 | 1 | 0
FRASER/TW | 0.061 | 0.0729 | 479.69 | 27.356 | 1 | 35/7 | 4.1783 | 132 | 526.9667 | 16 | 1699.5 | 2.9312 | 1 | 0
FRIGATE/SD | 0.0446 | 9999 | 684.81 | 35.281 | 1 | 22/7 | 4.4069 | 185 | 745.1598 | 21 | 2424.2 | 3.4976 | 1 | 0
GADWALL | 0.1909 | 9999 | 152.01 | 17.043 | 1 | 24/7 | 2.8397 | 63 | 171.9997 | 15 | 574.4 | 1.8948 | 1 | 0
GANNET | 0.0864 | 9999 | 337.77 | 25.756 | 1 | 26/7 | 4.0665 | 117 | 392.6444 | 16 | 1365.1 | 3.1623 | 1 | 0
GANNET/AW | 0.0778 | 0.0928 | 337.77 | 25.756 | 1 | 26/7 | 4.0665 | 116 | 392.6444 | 16 | 1299.2 | 3.1623 | 1 | 0
GARLIC | 0.1681 | 0.166 | 207 | 21.006 | 1 | 30/7 | 2.9997 | 87 | 261.4833 | 18 | 973 | 2.9997 | 1 | 0
GENESEE/TW | 0.0505 | 0.0601 | 586.76 | 29.591 | 1 | 33/7 | 4.7574 | 141 | 627.9342 | 15 | 1946.5 | 2.7381 | 1 | 0
GOAT | 0.1105 | 0.106 | 316.2 | 25.959 | 1 | 30/7 | 3.7109 | 135 | 399.6121 | 18 | 1491 | 3.7109 | 1 | 0
FLAMINGO | 0.0864 | 0.1031 | 337.77 | 25.4 | 1 | 24/7 | 4.2342 | 105 | 381.7412 | 15 | 1278.2 | 2.8219 | 1 | 0
CURLEW/TW | 0.0562 | 0.0606 | 523.67 | 28.677 | 1 | 22/7 | 5.5042 | 161 | 591.5472 | 13 | 1974.8 | 3.5128 | 1 | 0
IBIS/SD | 0.1435 | 9999 | 201.41 | 19.583 | 1 | 26/7 | 2.8905 | 73 | 233.9995 | 14 | 813.3 | 2.4409 | 1 | 0
CONDOR/TW | 0.0713 | 0.0853 | 402.83 | 25.222 | 1 | 20/7 | 5.0648 | 125 | 455.0313 | 12 | 1519.4 | 3.081 | 1 | 0
COOT | 0.0739 | 0.0882 | 402.83 | 26.416 | 1 | 36/1 | 3.7744 | 75 | 413.9347 | 18 | 1197.5 | 3.7744 | 1 | 0
CORN | 0.2423 | 0.239 | 144 | 17.501 | 1 | 30/7 | 2.4994 | 62 | 181.6125 | 18 | 675 | 2.4994 | 1 | 0
CORNCRAKE | 0.0615 | 0.0733 | 483.39 | 29.591 | 1 | 20/7 | 5.5474 | 114 | 516.7732 | 13 | 1599.8 | 2.4663 | 1 | 0
CRANE | 0.0665 | 0.0789 | 443.11 | 29.108 | 1 | 54/7 | 3.2334 | 140 | 501.0313 | 24 | 1675.7 | 3.2334 | 1 | 0
CRANE/AW | 0.0647 | 0.077 | 443.11 | 29.108 | 1 | 54/7 | 3.2334 | 136 | 501.0313 | 24 | 1608.7 | 3.2334 | 1 | 0
CREEPER/T2 | 0.0569 | 0.0675 | 523.67 | 35.636 | 1 | 20/7 | 4.0818 | 126 | 559.6763 | 13 | 1731.9 | 1.8136 | 1 | 0
CROW | 0.0795 | 0.0951 | 362.54 | 26.314 | 1 | 54/7 | 2.9235 | 117 | 409.0314 | 24 | 1370.6 | 2.9235 | 1 | 0
CROW/AW | 0.0787 | 0.094 | 362.54 | 26.314 | 1 | 54/7 | 2.9235 | 113 | 409.0314 | 24 | 1314.6 | 2.9235 | 1 | 0
CUCKOO | 0.0733 | 0.087 | 402.83 | 27.737 | 1 | 24/7 | 4.6228 | 124 | 455.0313 | 15 | 1523.9 | 3.081 | 1 | 0
CUMBERLAND/TW | 0.0311 | 0.0367 | 976.36 | 39.243 | 1 | 42/19 | 5.4407 | 290 | 1099.9333 | 18 | 3677.2 | 2.8778 | 1 | 0
CURLEW | 0.0565 | 0.0671 | 523.67 | 31.623 | 1 | 54/7 | 3.5128 | 163 | 591.1601 | 24 | 1979.3 | 3.5128 | 1 | 0
DUCK | 0.0953 | 9999 | 307.06 | 24.206 | 1 | 54/7 | 2.6899 | 100 | 347.0316 | 24 | 1159.3 | 2.6899 | 1 | 0
DOVE | 0.1031 | 0.123 | 281.98 | 23.546 | 1 | 26/7 | 3.716 | 101 | 327.9348 | 16 | 1139.9 | 2.8905 | 1 | 0
CONDOR/AW | 0.071 | 0.0846 | 402.83 | 27.737 | 1 | 54/7 | 3.081 | 124 | 454.7733 | 24 | 1460.3 | 3.081 | 1 | 0
DRAKE/AW | 0.0702 | 0.0836 | 402.83 | 28.143 | 1 | 26/7 | 4.4425 | 136 | 468.6442 | 16 | 1550.7 | 3.4544 | 1 | 0
DRAKE | 0.0727 | 0.0864 | 402.83 | 28.143 | 1 | 26/7 | 4.4425 | 140 | 468.6442 | 16 | 1628 | 3.4544 | 1 | 0
DOVE/TW | 0.1012 | 0.1214 | 281.98 | 21.641 | 1 | 20/7 | 4.2367 | 101 | 327.9348 | 12 | 1137.7 | 2.8905 | 1 | 0
DOVE/T2 | 0.0514 | 0.0618 | 563.45 | 38.532 | 1 | 26/7 | 3.716 | 201 | 655.8697 | 16 | 2279.9 | 2.8905 | 1 | 0
CURLEW/AW | 0.0551 | 0.0655 | 523.67 | 31.623 | 1 | 54/7 | 3.5128 | 157 | 591.1601 | 24 | 1897.4 | 3.5128 | 1 | 0
DOVE/AW | 0.0996 | 0.119 | 281.98 | 23.546 | 1 | 26/7 | 3.716 | 97 | 327.9348 | 16 | 1085 | 2.8905 | 1 | 0
CURLEW/SD | 0.0565 | 9999 | 523.67 | 30.251 | 1 | 54/7 | 5.4077 | 161 | 591.5472 | 14 | 1977.8 | 3.5128 | 1 | 0
DOG | 0.3321 | 0.396 | 103.7 | 14.173 | 1 | 6/7 | 4.7193 | 32 | 118.8385 | 6 | 394.8 | 1.5697 | 1 | 0
DIPPER/TW | 0.0437 | 0.0519 | 684.81 | 31.902 | 1 | 35/7 | 4.9911 | 163 | 732.1276 | 16 | 2265 | 2.9337 | 1 | 0
DIPPER/SD | 0.0446 | 9999 | 684.81 | 34.569 | 1 | 45/7 | 4.3205 | 163 | 731.6114 | 21 | 2265 | 2.9337 | 1 | 0
DIPPER/AW | 0.0441 | 0.052 | 684.55 | 35.204 | 1 | 45/7 | 4.4018 | 157 | 731.6114 | 21 | 2209.9 | 2.9337 | 1 | 0
DIPPER | 0.0446 | 0.0527 | 684.81 | 35.204 | 1 | 45/7 | 4.4018 | 161 | 731.6114 | 21 | 2266.5 | 2.9337 | 1 | 0
DRAKE/TW | 0.0711 | 0.0851 | 402.83 | 25.654 | 1 | 20/7 | 5.0648 | 141 | 468.4507 | 12 | 1625.1 | 3.4544 | 1 | 0
DOVE/SD | 0.1031 | 9999 | 281.98 | 23.343 | 1 | 26/7 | 4.097 | 101 | 327.9348 | 13 | 1138.4 | 2.8905 | 1 | 0
SUWANNEE/TW | 0.0591 | 0.0707 | 486.23 | 28.143 | 1 | 22/7 | 5.3035 | 165 | 565.2892 | 13 | 1961.4 | 3.7922 | 1 | 0
POWDER/TW | 0.0288 | 0.0337 | 1091.33 | 40.691 | 1 | 64/19 | 4.6584 | 272 | 1179.9976 | 22 | 3717.4 | 2.4409 | 1 | 0
RAIL/SD | 0.0618 | 9999 | 483.39 | 28.016 | 1 | 45/7 | 5.494 | 116 | 516.8377 | 13 | 1596.8 | 2.4663 | 1 | 0
RUDDY | 0.0659 | 0.0777 | 456.03 | 28.727 | 1 | 45/7 | 3.5916 | 109 | 487.4184 | 21 | 1510.5 | 2.3952 | 1 | 0
SWAN/T2 | 0.6755 | 0.8456 | 42.31 | 10.389 | 1 | 6/1 | 2.1184 | 17 | 49.3547 | 6 | 171.3 | 2.1184 | 1 | 0
RAIL/TW | 0.0608 | 0.0721 | 483.39 | 26.949 | 1 | 32/7 | 4.3866 | 115 | 516.8377 | 14 | 1599.8 | 2.4663 | 1 | 0
SWAN/AW | 1.3061 | 1.5634 | 21.13 | 6.35 | 1 | 6/1 | 2.1184 | 8 | 24.6451 | 6 | 81.3 | 2.1184 | 1 | 0
SWANATE/AW | 1.2713 | 1.5205 | 21.13 | 6.528 | 1 | 7/1 | 1.9609 | 10 | 26.5161 | 7 | 93.3 | 2.6137 | 1 | 0
SWALLOW/T2 | 0.5791 | 0.6742 | 53.3 | 11.684 | 1 | 6/1 | 2.38 | 20 | 62.1934 | 6 | 215.8 | 2.38 | 1 | 0
SWIFT | 0.092 | 0.1094 | 322.26 | 23.622 | 1 | 36/1 | 3.3757 | 61 | 331.1606 | 18 | 957.9 | 3.3757 | 1 | 0
STILT | 0.0805 | 9999 | 362.54 | 26.314 | 1 | 24/7 | 4.3866 | 113 | 409.9992 | 15 | 1372.1 | 2.9235 | 1 | 0
STARLING | 0.0802 | 0.0957 | 362.54 | 26.695 | 1 | 26/7 | 4.2139 | 126 | 421.6121 | 16 | 1465.5 | 3.2766 | 1 | 0
RAVEN | 0.5356 | 0.709 | 53.51 | 10.109 | 1 | 6/1 | 3.3706 | 19 | 62.4515 | 6 | 216.2 | 3.3706 | 1 | 0
ST CROIX/TW | 0.0407 | 0.0482 | 743.73 | 32.817 | 1 | 33/7 | 5.3569 | 159 | 782.192 | 15 | 2358.7 | 2.6441 | 1 | 0
WOODDUCK | 0.0941 | 9999 | 306.55 | 25.248 | 1 | 30/7 | 3.6068 | 131 | 375.9992 | 18 | 1398.9 | 3.6068 | 1 | 0
RAVEN/AW | 0.516 | 0.6175 | 53.56 | 10.109 | 1 | 6/1 | 3.3706 | 19 | 62.4515 | 6 | 205.7 | 3.3706 | 1 | 0
RAVEN/T2 | 0.2919 | 0.3542 | 107.02 | 16.561 | 1 | 6/1 | 3.3706 | 39 | 124.903 | 6 | 432.2 | 3.3706 | 1 | 0
SWAN | 1.3515 | 1.7119 | 21.15 | 6.35 | 1 | 6/1 | 2.1184 | 8 | 24.6451 | 6 | 85.4 | 2.1184 | 1 | 0
WOLF | 0.2263 | 0.223 | 154.3 | 18.136 | 1 | 30/7 | 2.5908 | 67 | 195.0319 | 18 | 727.6 | 2.5908 | 1 | 0
WABASH/TW | 0.074 | 0.0887 | 386.51 | 25.146 | 1 | 20/7 | 4.9606 | 136 | 449.4185 | 12 | 1558.1 | 3.3807 | 1 | 0
WAXWING | 0.2156 | 0.2585 | 135.19 | 15.469 | 1 | 18/1 | 3.0912 | 31 | 142.5804 | 12 | 430.8 | 3.0912 | 1 | 0
WAXWING/AW | 0.2134 | 0.2551 | 135.19 | 15.469 | 1 | 18/1 | 3.0912 | 30 | 142.5804 | 12 | 421.9 | 3.0912 | 1 | 0
PTARMIGAN/T2 | 0.0729 | 0.0868 | 402.83 | 31.267 | 1 | 20/7 | 3.5585 | 99 | 430.9669 | 13 | 1318.8 | 1.59 | 1 | 0
WAXWING/T2 | 0.1079 | 0.1288 | 270.38 | 25.324 | 1 | 18/1 | 3.0912 | 61 | 285.1607 | 12 | 861.3 | 3.0912 | 1 | 0
PUFFIN | 0.0733 | 9999 | 402.83 | 27.356 | 1 | 22/7 | 4.8285 | 110 | 442.3862 | 14 | 1425.7 | 2.6822 | 1 | 0
SWANATE | 1.3359 | 1.6945 | 21.15 | 6.528 | 1 | 7/1 | 1.9609 | 10 | 26.5161 | 7 | 99.7 | 2.6137 | 1 | 0
WILLET | 0.0672 | 9999 | 443.11 | 28.321 | 1 | 45/7 | 3.5408 | 111 | 473.9991 | 21 | 1468.8 | 2.3597 | 1 | 0
SQUAB | 0.0951 | 0.1131 | 306.55 | 24.536 | 1 | 26/7 | 3.8735 | 108 | 356.2574 | 16 | 1238.6 | 3.0124 | 1 | 0
PUFFIN/SD | 0.0733 | 9999 | 402.83 | 26.264 | 1 | 22/7 | 5.1638 | 112 | 442.3862 | 12 | 1422.7 | 2.6822 | 1 | 0
PUFFIN/TW | 0.0716 | 0.0857 | 402.83 | 24.892 | 1 | 18/7 | 5.3391 | 115 | 446.3862 | 10 | 1451.4 | 2.8143 | 1 | 0
QUAIL | 0.4269 | 0.5773 | 67.44 | 11.354 | 1 | 6/1 | 3.7846 | 24 | 78.774 | 6 | 272.6 | 3.7846 | 1 | 0
QUAIL/T2 | 0.238 | 0.2858 | 134.88 | 18.593 | 1 | 6/1 | 3.7821 | 47 | 157.29 | 6 | 544.5 | 9999 | 1 | 0
RACOON | 0.4432 | 0.46 | 77.8 | 12.268 | 1 | 6/1 | 4.0894 | 27 | 91.9353 | 6 | 318.2 | 4.0894 | 1 | 0
SWIFT/TW | 0.0908 | 0.1086 | 322.26 | 21.59 | 1 | 27/1 | 3.8989 | 60 | 331.1606 | 13 | 961.4 | 3.3757 | 1 | 0
RAIL | 0.0618 | 0.0733 | 483.39 | 29.591 | 1 | 45/7 | 3.6982 | 115 | 516.7732 | 21 | 1601.3 | 2.4663 | 1 | 0
WIDGEON | 0.1708 | 9999 | 170.45 | 18.034 | 1 | 24/7 | 3.0074 | 56 | 193.0319 | 15 | 644.4 | 2.0015 | 1 | 0
ROOK/SD | 0.0907 | 9999 | 322.26 | 24.257 | 1 | 24/7 | 4.5872 | 102 | 363.9993 | 12 | 1217.3 | 2.7559 | 1 | 0
ROBIN/AW | 0.6506 | 0.778 | 42.41 | 8.992 | 1 | 6/1 | 2.9997 | 16 | 49.4838 | 6 | 163 | 2.9997 | 1 | 0
SCOTER | 0.0895 | 9999 | 322.26 | 25.883 | 1 | 30/7 | 3.6982 | 137 | 397.0315 | 18 | 1477.7 | 3.6982 | 1 | 0
ROBIN/T2 | 0.364 | 0.4238 | 84.82 | 14.757 | 1 | 6/1 | 2.9997 | 32 | 98.9675 | 6 | 342.6 | 2.9997 | 1 | 0
ROOK | 0.0907 | 0.1081 | 322.26 | 24.816 | 1 | 24/7 | 4.1351 | 101 | 364.0638 | 15 | 1219.1 | 2.7559 | 1 | 0
SCISSORTL/SD | 0.0478 | 9999 | 644.52 | 33.147 | 1 | 42/7 | 4.1427 | 140 | 677.6115 | 21 | 2041.8 | 2.4562 | 1 | 0
SCISSORTAIL/TW | 0.0464 | 0.0552 | 644.52 | 30.556 | 1 | 30/7 | 5.2299 | 140 | 677.7406 | 14 | 2041.8 | 2.4562 | 1 | 0
REDBIRD | 0.0609 | 0.0727 | 483.39 | 30.378 | 1 | 24/7 | 5.0648 | 149 | 546.1925 | 15 | 1828.9 | 3.3757 | 1 | 0
ROOK/AW | 0.0884 | 0.1054 | 322.26 | 24.816 | 1 | 24/7 | 4.1351 | 98 | 364.0638 | 15 | 1169.1 | 0.4699 | 1 | 0
SMEW/SD | 0.0349 | 9999 | 901.93 | 38.887 | 1 | 76/7 | 4.8616 | 194 | 946.4497 | 21 | 2858.8 | 2.9058 | 1 | 0
ROOK/T2 | 0.046 | 9999 | 644.52 | 40.615 | 1 | 24/7 | 4.1351 | 202 | 728.1276 | 24 | 2437.6 | 4.1351 | 1 | 0
SANTEE/TW | 0.0245 | 0.0285 | 1331.25 | 44.755 | 1 | 64/19 | 5.146 | 331 | 1436.6423 | 22 | 4535.9 | 2.6975 | 1 | 0
ROOK/TW | 0.089 | 0.1067 | 322.26 | 22.606 | 1 | 19/7 | 4.6482 | 102 | 364.0638 | 11 | 1214.3 | 2.7559 | 1 | 0
STARLING/AW | 0.0778 | 0.0928 | 362.8 | 26.695 | 1 | 26/7 | 4.2139 | 122 | 421.6121 | 16 | 1394.9 | 3.2766 | 1 | 0
YUKON/TW | 0.0471 | 0.0561 | 625.07 | 31.623 | 1 | 38/19 | 4.5771 | 191 | 704.8373 | 16 | 2360.2 | 2.3114 | 1 | 0
ZEBRA | 0.0815 | 0.0802 | 417.29 | 28.575 | 1 | 54/7 | 3.1801 | 130 | 482.9668 | 24 | 1618.9 | 3.1801 | 1 | 0
RUDDY/AW | 0.0645 | 0.0767 | 456.03 | 28.727 | 1 | 45/7 | 3.5916 | 107 | 487.4184 | 21 | 1471.6 | 2.3952 | 1 | 0
SCHUYKILL/TW | 0.0363 | 0.0429 | 839.8 | 35.204 | 1 | 36/7 | 5.4508 | 196 | 898.0627 | 16 | 2779.9 | 3.2512 | 1 | 0
SPARATE | 0.8407 | 1.0818 | 33.62 | 8.255 | 1 | 7/1 | 2.474 | 16 | 42.1935 | 7 | 158.8 | 3.2995 | 1 | 0
RAIL/AW | 0.061 | 0.0725 | 483.39 | 29.591 | 1 | 45/7 | 3.6982 | 113 | 516.7732 | 21 | 1561.1 | 2.4663 | 1 | 0
REDSTART | 0.0646 | 9999 | 456.03 | 29.515 | 1 | 24/7 | 4.9174 | 141 | 514.9022 | 15 | 1724.8 | 3.2791 | 1 | 0
REDWING | 0.0795 | 0.0951 | 362.54 | 27.457 | 1 | 30/19 | 3.9218 | 154 | 444.9023 | 18 | 1651.9 | 2.352 | 1 | 0
SPARROW/T2 | 0.4591 | 0.5467 | 67.24 | 13.132 | 1 | 6/1 | 2.6721 | 25 | 78.4515 | 6 | 271.9 | 2.6721 | 1 | 0
SPARROW/AW | 0.8208 | 0.9824 | 33.64 | 8.026 | 1 | 6/1 | 2.6721 | 13 | 39.2257 | 6 | 129.2 | 2.6721 | 1 | 0
SPARROW | 0.85 | 1.1023 | 33.62 | 8.026 | 1 | 6/1 | 2.6721 | 13 | 39.2257 | 6 | 135.9 | 2.6721 | 1 | 0
COYOTE | 0.226 | 0.267 | 132.1 | 15.9 | 1 | 26/7 | 2.54 | 47 | 152.1932 | 16 | 521.5 | 1.9101 | 1 | 0
ROBIN | 0.6754 | 0.8867 | 42.41 | 8.992 | 1 | 6/1 | 2.9997 | 16 | 49.4838 | 6 | 171.3 | 2.9997 | 1 | 0
REDWING/AW | 0.0763 | 0.0911 | 362.54 | 27.457 | 1 | 30/19 | 3.9218 | 149 | 444.9023 | 18 | 1553.6 | 2.352 | 1 | 0
SKIMMER | 0.0721 | 9999 | 402.83 | 28.956 | 1 | 30/7 | 4.1351 | 170 | 497.0313 | 18 | 1854.2 | 4.1351 | 1 | 0
SNOWBIRD/TW | 0.0564 | 0.0673 | 523.67 | 27.661 | 1 | 30/7 | 4.7142 | 114 | 550.5795 | 14 | 1659.3 | 2.2123 | 1 | 0
RICE | 0.0365 | 0.0414 | 935.98 | 42.799 | 1 | 54/19 | 4.7498 | 277 | 1077.9978 | 24 | 3600 | 2.8499 | 1 | 0
RINGDOVE/SD | 0.0451 | 9999 | 684.81 | 33.884 | 1 | 42/7 | 4.2672 | 149 | 719.9986 | 21 | 2169.7 | 2.5324 | 1 | 0
RIO GRANDE/TW | 0.0384 | 0.0456 | 776.92 | 35.103 | 1 | 39/19 | 5.0368 | 237 | 875.5466 | 17 | 2928.7 | 2.5705 | 1 | 0
SNOWBIRD/SD | 0.058 | 9999 | 523.67 | 30.099 | 1 | 42/7 | 3.7617 | 115 | 550.5795 | 21 | 1659.3 | 2.2123 | 1 | 0
SNOWBIRD | 0.0575 | 9999 | 523.67 | 30.556 | 1 | 42/7 | 3.9853 | 113 | 550.9021 | 21 | 1659.9 | 2.2149 | 1 | 0
SQUAB/AW | 0.0918 | 0.1096 | 306.55 | 24.536 | 1 | 26/7 | 3.8735 | 105 | 356.2574 | 16 | 1178.8 | 3.0124 | 1 | 0
SPARATE/AW | 0.7985 | 0.955 | 33.64 | 8.255 | 1 | 7/1 | 2.474 | 16 | 42.1935 | 7 | 148.7 | 3.2995 | 1 | 0
TERN | 0.0739 | 0.0876 | 402.83 | 27 | 1 | 45/7 | 3.3757 | 98 | 430.5798 | 21 | 1333.1 | 2.2504 | 1 | 0
PLOVER/SD | 0.0418 | 9999 | 725.09 | 36.779 | 1 | 54/19 | 4.0869 | 221 | 817.4177 | 24 | 2730.8 | 2.4816 | 1 | 0
PLOVER/AW | 0.0409 | 0.0483 | 725.09 | 37.211 | 1 | 54/19 | 4.1351 | 212 | 817.4177 | 24 | 2628.1 | 2.4816 | 1 | 0
TATLER/T2 | 0.0613 | 0.0073 | 483.39 | 34.214 | 1 | 20/7 | 3.9218 | 117 | 516.7086 | 13 | 1598.9 | 1.7424 | 1 | 0
TEAL | 0.0938 | 0.1125 | 306.55 | 25.248 | 1 | 30/19 | 3.6068 | 133 | 376.3863 | 18 | 1398.1 | 2.1641 | 1 | 0
PHEASANT | 0.0467 | 0.0553 | 644.52 | 35.103 | 1 | 54/19 | 3.8989 | 194 | 726.4502 | 24 | 2433.1 | 2.3393 | 1 | 0
PIPER | 0.1889 | 9999 | 152.01 | 17.78 | 1 | 30/7 | 2.54 | 69 | 187.0319 | 18 | 699.4 | 2.54 | 1 | 0
THAMES/TW | 0.0437 | 0.052 | 676.24 | 32.766 | 1 | 39/19 | 4.699 | 206 | 761.8694 | 17 | 2549.2 | 2.3978 | 1 | 0
PLOVER | 0.0418 | 0.0495 | 725.09 | 37.211 | 1 | 54/19 | 4.1351 | 218 | 817.4177 | 24 | 2738.2 | 2.4816 | 1 | 0
PLATTE/TW | 0.0383 | 0.0454 | 795.01 | 33.884 | 1 | 33/7 | 5.5372 | 170 | 835.9338 | 15 | 2519.5 | 2.728 | 1 | 0
TEAL/AW | 0.09 | 0.1074 | 306.55 | 25.248 | 1 | 30/19 | 3.6068 | 127 | 376.3863 | 18 | 1314.3 | 2.1641 | 1 | 0
THRASHER/AW | 0.0281 | 0.0326 | 1171.49 | 45.771 | 1 | 76/19 | 4.4298 | 246 | 1235.0943 | 28 | 3683.2 | 2.0676 | 1 | 0
PHEASANT/SD | 0.0467 | 9999 | 644.52 | 35.001 | 1 | 54/19 | 4.3764 | 196 | 726.4502 | 21 | 2428.7 | 2.3393 | 1 | 0
THRASHER | 0.0282 | 0.0328 | 1171.49 | 45.771 | 1 | 76/19 | 4.4298 | 252 | 1235.0943 | 28 | 3759.1 | 2.0676 | 1 | 0
PIPIT/SD | 0.0925 | 9999 | 322.26 | 22.708 | 1 | 42/7 | 4.9073 | 69 | 338.838 | 11 | 1017.9 | 1.7374 | 1 | 0
PHEASANT/TW | 0.0457 | 0.0544 | 644.52 | 32.106 | 1 | 39/19 | 4.5872 | 196 | 726.1921 | 17 | 2428.7 | 2.3393 | 1 | 0
PHOEBE | 0.192 | 9999 | 152.01 | 16.408 | 1 | 18/1 | 3.2791 | 34 | 159.9997 | 12 | 485.1 | 3.2791 | 1 | 0
TERN/TW | 0.0721 | 0.0862 | 402.83 | 24.384 | 1 | 17/7 | 5.494 | 97 | 430.6443 | 9 | 1327.4 | 2.2504 | 1 | 0
PHOENIX/SD | 0.0622 | 9999 | 483.39 | 27.635 | 1 | 42/7 | 5.5321 | 105 | 508.1925 | 13 | 1528.3 | 2.1234 | 1 | 0
PHOENIX/TW | 0.061 | 0.0728 | 483.39 | 26.518 | 1 | 30/7 | 4.5288 | 105 | 508.128 | 14 | 1535.8 | 2.126 | 1 | 0
PIGEON | 0.3393 | 0.4741 | 85.02 | 12.751 | 1 | 6/1 | 4.2469 | 29 | 99.1611 | 6 | 343.5 | 4.2469 | 1 | 0
PIGEON/T2 | 0.193 | 0.2113 | 170.05 | 20.879 | 1 | 6/1 | 4.2469 | 59 | 198.4512 | 6 | 686.6 | 4.2469 | 1 | 0
TERN/AW | 0.0726 | 0.0866 | 402.83 | 27 | 1 | 45/7 | 3.3757 | 96 | 430.5798 | 21 | 1299.8 | 2.2504 | 1 | 0
TERN/SD | 0.0739 | 9999 | 402.83 | 25.73 | 1 | 45/7 | 5.4458 | 97 | 430.7088 | 11 | 1328.9 | 2.2504 | 1 | 0
PHEASANT/AW | 0.0455 | 0.054 | 644.52 | 35.103 | 1 | 54/19 | 3.8989 | 189 | 726.4502 | 24 | 2336.4 | 2.3393 | 1 | 0
TIGER | 0.272 | 0.255 | 128.3 | 16.535 | 1 | 30/7 | 2.3597 | 57 | 162.1287 | 18 | 605.2 | 2.3597 | 1 | 0
TURNSTONE | 0.0654 | 9999 | 456.03 | 28.727 | 1 | 20/7 | 5.3873 | 107 | 487.4184 | 13 | 1510.5 | 2.3952 | 1 | 0
PLOVER/TW | 0.0409 | 0.0487 | 725.09 | 33.96 | 1 | 37/19 | 4.9962 | 221 | 817.0306 | 17 | 2732.3 | 2.4816 | 1 | 0
PENGUIN/T2 | 0.1607 | 0.1863 | 214.44 | 23.419 | 1 | 6/1 | 4.7701 | 74 | 250.193 | 6 | 866.3 | 4.7701 | 1 | 0
TURKEY | 2.1499 | 0.2585 | 13.3 | 5.029 | 1 | 6/1 | 1.6789 | 5 | 15.4838 | 6 | 53.7 | 1.6789 | 1 | 0
POPINJAY/SD | 0.0429 | 9999 | 725.09 | 35.077 | 1 | 42/7 | 4.384 | 157 | 760.6436 | 21 | 2297.7 | 2.6035 | 1 | 0
TURKEY/AW | 2.1493 | 2.6769 | 13.28 | 5.029 | 1 | 6/1 | 1.6789 | 5 | 15.4838 | 6 | 51 | 1.6789 | 1 | 0
PETREL | 0.5331 | 0.7854 | 51.58 | 11.709 | 1 | 12/7 | 2.3393 | 46 | 81.6127 | 12 | 378.1 | 2.3393 | 1 | 0
POTATO | 0.0583 | 0.063 | 582.99 | 33.807 | 1 | 54/19 | 3.749 | 177 | 671.6761 | 24 | 2250 | 2.2504 | 1 | 0
TRUCKEE/TW | 0.0433 | 0.0513 | 695.45 | 31.699 | 1 | 30/7 | 5.4331 | 149 | 731.2243 | 14 | 2204 | 2.5502 | 1 | 0
PENGUIN/AW | 0.2578 | 0.3085 | 107.22 | 14.3 | 1 | 6/1 | 4.7701 | 37 | 125.0965 | 6 | 411.9 | 4.7701 | 1 | 0
PENGUIN | 0.2697 | 0.3797 | 107.22 | 14.3 | 1 | 6/1 | 4.7701 | 37 | 125.0965 | 6 | 433.2 | 4.7701 | 1 | 0
POTOMAC/TW | 0.0383 | 0.0454 | 789.13 | 34.163 | 1 | 36/7 | 5.2832 | 186 | 843.8048 | 16 | 2611.7 | 3.1521 | 1 | 0
TURBIT | 0.0736 | 9999 | 402.83 | 27 | 1 | 20/7 | 5.0648 | 97 | 430.8378 | 13 | 1333.4 | 2.2504 | 1 | 0
FLAMINGO/ACSS | 0.0842 | 0.101 | 337.77 | 25.4 | 2 | 24/7 | 4.2342 | 81 | 381.5476 | 15 | 1276.8 | 2.8219 | 1 | 0
RUDDY/ACSS/AW | 0.0628 | 0.0756 | 456.03 | 28.727 | 2 | 45/7 | 3.5916 | 68 | 487.4184 | 21 | 1469.7 | 2.3952 | 1 | 0
FLICKER/ACSS/TW | 0.1166 | 0.1401 | 241.7 | 19.71 | 2 | 18/7 | 4.1351 | 58 | 273.0962 | 10 | 911.9 | 2.3876 | 1 | 0
FLICKER/ACSS/AW | 0.1142 | 0.1371 | 241.7 | 21.488 | 2 | 24/7 | 3.5814 | 56 | 273.0317 | 15 | 876.2 | 2.3876 | 1 | 0
TOWHEE/ACSS/AW | 0.0589 | 0.0703 | 483.39 | 29.845 | 2 | 48/7 | 3.5814 | 85 | 526.257 | 22 | 1620 | 2.7864 | 1 | 0
FLICKER/ACSS | 0.1171 | 0.1407 | 241.7 | 21.488 | 2 | 24/7 | 3.5814 | 58 | 273.0317 | 15 | 915.2 | 2.3876 | 1 | 0
SNOWBIRD/ACSS/TW | 0.0559 | 0.0666 | 523.67 | 27.661 | 2 | 30/7 | 4.7142 | 69 | 550.5795 | 14 | 1659.3 | 2.2123 | 1 | 0
CHUKAR/ACSS/TW | 0.0337 | 0.0397 | 901.93 | 36.703 | 2 | 37/19 | 5.5702 | 157 | 975.4819 | 17 | 3067.1 | 2.22 | 1 | 0
SANTEE/ACSS/TW | 0.0246 | 0.0285 | 1331.25 | 44.755 | 2 | 64/19 | 5.146 | 228 | 1436.6423 | 22 | 4535.9 | 2.6975 | 1 | 0
FLAMINGO/ACSS/AW | 0.0821 | 0.0985 | 337.77 | 25.4 | 2 | 24/7 | 4.2342 | 78 | 381.5476 | 15 | 1224.6 | 2.8219 | 1 | 0
CARDINAL/ACSS | 0.0594 | 0.0731 | 483.39 | 30.378 | 2 | 54/7 | 3.3757 | 116 | 545.9989 | 24 | 1828.9 | 3.3757 | 1 | 0
BITTERN/ACSS | 0.0459 | 0.0549 | 644.52 | 34.163 | 2 | 45/7 | 4.2697 | 99 | 689.0309 | 21 | 2134 | 2.8473 | 1 | 0
COLUMBIA/ACSS/TW | 0.0584 | 0.0698 | 489.57 | 27.737 | 2 | 21/7 | 5.4483 | 117 | 553.0957 | 13 | 1846.8 | 3.3985 | 1 | 0
CANVASBACK/ACSS/AW | 0.0561 | 0.0671 | 483.39 | 31.699 | 2 | 30/19 | 4.5288 | 175 | 593.4827 | 18 | 2070.9 | 2.7178 | 1 | 0
SNOWBIRD/ACSS/AW | 0.0554 | 0.0661 | 523.67 | 30.556 | 2 | 42/7 | 3.9853 | 66 | 550.9021 | 20 | 1627.7 | 2.2149 | 1 | 0
CANVASBACK/ACSS | 0.0585 | 0.0701 | 483.39 | 31.699 | 2 | 30/19 | 4.5288 | 183 | 593.4827 | 18 | 2202.6 | 2.7178 | 1 | 0
YUKON/ACSS/TW | 0.0465 | 0.0555 | 625.07 | 31.623 | 2 | 38/19 | 4.5771 | 148 | 704.8373 | 16 | 2360.2 | 2.3114 | 1 | 0
FINCH/ACSS/TW | 0.0513 | 0.0613 | 563.96 | 30.099 | 2 | 38/19 | 4.4983 | 135 | 635.5471 | 16 | 2126.6 | 2.1895 | 1 | 0
FINCH/ACSS/AW | 0.0503 | 0.0617 | 563.96 | 32.842 | 2 | 54/19 | 3.6474 | 128 | 635.7407 | 24 | 2042.6 | 2.1895 | 1 | 0
FINCH/ACSS | 0.0516 | 0.0632 | 563.96 | 32.842 | 2 | 54/19 | 3.6474 | 135 | 635.7407 | 24 | 2129.6 | 2.1895 | 1 | 0
CARDINAL/ACSS/AW | 0.058 | 0.0713 | 483.39 | 30.378 | 2 | 54/7 | 3.3757 | 109 | 545.9989 | 24 | 1751.4 | 3.3757 | 1 | 0
FALCON/ACSS/TW | 0.0368 | 0.0436 | 805.65 | 35.763 | 2 | 42/19 | 4.9428 | 189 | 907.8046 | 18 | 3032.9 | 2.6162 | 1 | 0
SAPSUCKER/ACSS/AW | 0.0964 | 0.119 | 281.98 | 22.885 | 2 | 22/7 | 4.0386 | 53 | 309.4833 | 14 | 962.7 | 2.2428 | 1 | 0
SCHUYKILL/ACSS/TW | 0.0361 | 0.0426 | 839.8 | 35.204 | 2 | 36/7 | 5.4508 | 129 | 898.0627 | 16 | 2779.9 | 3.2512 | 1 | 0
GRACKLE/ACSS/TW | 0.048 | 0.0574 | 604.24 | 31.115 | 2 | 38/19 | 4.4983 | 145 | 680.9019 | 16 | 2276.9 | 2.2657 | 1 | 0
GRACKLE/ACSS/AW | 0.0472 | 0.0577 | 604.24 | 33.985 | 2 | 54/19 | 3.7744 | 137 | 680.6438 | 24 | 2187.4 | 2.2657 | 1 | 0
SAPSUCKER/ACSS | 0.101 | 0.1213 | 281.98 | 22.885 | 2 | 22/7 | 4.0386 | 56 | 309.4833 | 14 | 995.6 | 2.2428 | 1 | 0
GRACKLE/ACSS | 0.0483 | 0.0591 | 604.24 | 33.985 | 2 | 54/19 | 3.7744 | 145 | 680.6438 | 24 | 2281.3 | 2.2657 | 1 | 0
CHEYENNE/ACSS/TW | 0.0498 | 0.0593 | 591.88 | 29.337 | 2 | 30/7 | 5.0114 | 77 | 622.3213 | 14 | 1875.1 | 2.352 | 1 | 0
SCISSORTAIL/ACSS/TW | 0.046 | 0.0547 | 644.52 | 30.556 | 2 | 30/7 | 5.2299 | 83 | 677.7406 | 14 | 2041.8 | 2.4562 | 1 | 0
GOLDFINCH/ACSS/AW | 0.087 | 0.1043 | 322.26 | 24.46 | 2 | 22/7 | 4.318 | 60 | 353.8057 | 14 | 1100.3 | 2.3978 | 1 | 0
GOLDFINCH/ACSS | 0.0886 | 0.1063 | 322.26 | 24.46 | 2 | 22/7 | 4.318 | 63 | 353.8057 | 14 | 1138.1 | 2.3978 | 1 | 0
CARDINAL/ACSS/TW | 0.0592 | 0.0707 | 483.39 | 27.534 | 2 | 20/7 | 5.5474 | 116 | 546.0634 | 12 | 1824.5 | 3.3757 | 1 | 0
CHUKAR/ACSS/AW | 0.0336 | 0.0395 | 902.43 | 40.691 | 2 | 84/19 | 3.6982 | 149 | 976.1271 | 30 | 2995.7 | 2.22 | 1 | 0
THRASHER/ACSS | 0.0278 | 0.0322 | 1171.49 | 45.771 | 2 | 76/19 | 4.4298 | 158 | 1235.0943 | 28 | 3755.1 | 2.0676 | 1 | 0
SNOWBIRD/ACSS | 0.056 | 0.0667 | 523.67 | 30.556 | 2 | 42/7 | 3.9853 | 69 | 550.9021 | 20 | 1659.9 | 2.2149 | 1 | 0
GANNET/ACSS/AW | 0.0812 | 0.0974 | 337.77 | 25.756 | 2 | 26/7 | 4.0665 | 93 | 389.4831 | 16 | 1298 | 3.1623 | 1 | 0
GANNET/ACSS | 0.0838 | 0.1005 | 337.77 | 25.756 | 2 | 26/7 | 4.0665 | 97 | 389.4831 | 16 | 1364.6 | 3.1623 | 1 | 0
THAMES/ACSS/TW | 0.0432 | 0.0514 | 676.24 | 32.766 | 2 | 39/19 | 4.699 | 159 | 761.8694 | 17 | 2549.2 | 2.3978 | 1 | 0
SCOTER/ACSS | 0.0871 | 0.1045 | 322.26 | 25.883 | 2 | 30/7 | 3.6982 | 122 | 397.4186 | 18 | 1480.9 | 3.6982 | 1 | 0
TOWHEE/ACSS | 0.0599 | 0.0716 | 483.39 | 29.845 | 2 | 48/7 | 3.5814 | 88 | 526.257 | 22 | 1670.9 | 2.7864 | 1 | 0
CATAWBA/ACSS/TW | 0.046 | 0.0547 | 644.52 | 30.556 | 2 | 30/7 | 5.2299 | 83 | 677.7406 | 14 | 2041.8 | 2.4562 | 1 | 0
SCOTER/ACSS/AW | 0.0833 | 0.0999 | 322.26 | 25.883 | 2 | 30/7 | 3.6982 | 112 | 397.4186 | 18 | 1391.1 | 3.6982 | 1 | 0
CHUKAR/ACSS | 0.034 | 0.0401 | 902.43 | 40.691 | 2 | 84/19 | 3.6982 | 157 | 976.1271 | 30 | 3087.9 | 2.22 | 1 | 0
GROSBEAK/ACSS/AW | 0.0851 | 0.102 | 322.26 | 25.146 | 2 | 26/7 | 3.9726 | 89 | 374.7734 | 16 | 1238.4 | 3.0886 | 1 | 0
FRASER/ACSS/TW | 0.0602 | 0.072 | 479.69 | 27.356 | 2 | 35/7 | 4.1783 | 94 | 526.9667 | 16 | 1699.5 | 2.9312 | 1 | 0
GENESEE/ACSS/TW | 0.05 | 0.0596 | 586.76 | 29.591 | 2 | 33/7 | 4.7574 | 91 | 627.9342 | 15 | 1946.5 | 2.7381 | 1 | 0
THRASHER/ACSS/AW | 0.0275 | 0.0319 | 1171.49 | 45.771 | 2 | 76/19 | 4.4298 | 152 | 1235.0943 | 28 | 3678.9 | 2.0676 | 1 | 0
TAILORBIRD/ACSS/AW | 0.1166 | 0.14 | 241.7 | 20.93 | 2 | 20/7 | 3.9218 | 36 | 258.3221 | 13 | 778.8 | 1.7424 | 1 | 0
CUCKOO/ACSS | 0.0709 | 0.0849 | 402.83 | 27.737 | 2 | 24/7 | 4.6228 | 97 | 455.0313 | 15 | 1521.9 | 3.081 | 1 | 0
CUCKOO/ACSS/AW | 0.0692 | 0.0828 | 402.83 | 27.737 | 2 | 24/7 | 4.6228 | 93 | 455.0313 | 15 | 1459.7 | 3.081 | 1 | 0
CUMBERLAND/ACSS/TW | 0.031 | 0.0365 | 976.36 | 39.243 | 2 | 42/19 | 5.4407 | 230 | 1099.9333 | 18 | 3677.2 | 2.8778 | 1 | 0
CURLEW/ACSS | 0.0551 | 0.0675 | 523.67 | 31.623 | 2 | 54/7 | 3.5128 | 125 | 591.1601 | 24 | 1979.3 | 3.5128 | 1 | 0
CURLEW/ACSS/AW | 0.0537 | 0.0659 | 523.67 | 31.623 | 2 | 54/7 | 3.5128 | 116 | 591.1601 | 24 | 1896.7 | 3.5128 | 1 | 0
EAGLE/ACSS/AW | 0.0951 | 0.114 | 281.98 | 24.206 | 2 | 30/7 | 3.4595 | 102 | 347.8058 | 18 | 1217.5 | 3.4595 | 1 | 0
TRUCKEE/ACSS/TW | 0.0429 | 0.0509 | 695.45 | 31.699 | 2 | 30/7 | 5.4331 | 90 | 731.2243 | 14 | 2204 | 2.5502 | 1 | 0
CANARY/ACSS | 0.0629 | 0.0774 | 456.03 | 28.981 | 2 | 54/7 | 3.2791 | 109 | 515.1603 | 24 | 1724.8 | 3.2791 | 1 | 0
BLUEBIRD/ACSS/AW | 0.0286 | 0.0334 | 1092.45 | 44.755 | 2 | 84/19 | 4.0691 | 181 | 1181.2234 | 30 | 3625.9 | 2.4409 | 1 | 0
GROSBEAK/ACSS/TW | 0.0874 | 0.1049 | 322.26 | 23.063 | 2 | 20/7 | 4.5288 | 92 | 374.7089 | 12 | 1299.9 | 3.0886 | 1 | 0
TEAL/ACSS | 0.0915 | 0.1098 | 306.55 | 25.248 | 2 | 30/19 | 3.6068 | 118 | 376.4509 | 18 | 1398.9 | 2.1641 | 1 | 0
WOOD DUCK/ACSS/AW | 0.0875 | 0.1049 | 306.55 | 25.248 | 2 | 30/7 | 3.6068 | 109 | 378.0638 | 18 | 1323.3 | 3.6068 | 1 | 0
CORNCRAKE/ACSS/AW | 0.0594 | 0.0709 | 483.39 | 29.591 | 2 | 20/7 | 19.0297 | 72 | 516.7732 | 13 | 1558.4 | 2.4663 | 1 | 0
DIPPER/ACSS | 0.0434 | 0.0519 | 684.81 | 35.204 | 2 | 45/7 | 4.4018 | 105 | 731.6114 | 21 | 2266.5 | 2.9337 | 1 | 0
CURLEW/ACSS/TW | 0.0547 | 0.0654 | 523.67 | 28.677 | 2 | 22/7 | 5.5042 | 125 | 591.5472 | 13 | 1974.8 | 3.5128 | 1 | 0
BLUEJAY/ACSS/TW | 0.0519 | 0.0619 | 563.96 | 29.032 | 2 | 33/7 | 4.6634 | 87 | 603.0311 | 15 | 1870.6 | 2.6645 | 1 | 0
BRANT/ACSS | 0.1714 | 0.1686 | 201.41 | 19.609 | 2 | 24/7 | 3.269 | 49 | 227.4189 | 15 | 761.9 | 2.1793 | 1 | 0
WABASH/ACSS/TW | 0.0709 | 0.0877 | 386.51 | 25.146 | 2 | 20/7 | 4.9606 | 111 | 449.4185 | 12 | 1558.1 | 3.3807 | 1 | 0
BOBOLINK/ACSS/TW | 0.0411 | 0.0488 | 725.09 | 32.791 | 2 | 36/7 | 5.0648 | 112 | 775.2888 | 16 | 2397.4 | 3.0201 | 1 | 0
BOBOLINK/ACSS/AW | 0.0408 | 0.0485 | 725.09 | 36.246 | 2 | 45/7 | 4.5288 | 108 | 774.8372 | 21 | 2337.2 | 3.0201 | 1 | 0
BOBOLINK/ACSS | 0.0413 | 0.0492 | 725.09 | 36.246 | 2 | 45/7 | 4.5288 | 112 | 774.8372 | 21 | 2400.4 | 3.0201 | 1 | 0
BUNTING/ACSS | 0.0488 | 0.0583 | 604.24 | 33.071 | 2 | 45/7 | 4.1351 | 93 | 645.8052 | 21 | 2000.1 | 2.7559 | 1 | 0
TAILORBIRD/ACSS | 0.1181 | 0.1419 | 241.7 | 20.93 | 2 | 20/7 | 3.9218 | 38 | 258.3221 | 13 | 798.7 | 1.7424 | 1 | 0
BUNTING/ACSS/TW | 0.0487 | 0.0579 | 604.24 | 29.997 | 2 | 33/7 | 4.8285 | 93 | 645.9987 | 15 | 1998.6 | 2.7559 | 1 | 0
CANARY/ACSS/AW | 0.0613 | 0.0754 | 456.03 | 28.981 | 2 | 54/7 | 3.2791 | 103 | 515.1603 | 24 | 1652.8 | 3.2791 | 1 | 0
BLUEJAY/ACSS/AW | 0.0513 | 0.0615 | 563.96 | 31.953 | 2 | 45/7 | 3.9954 | 84 | 603.2246 | 21 | 1818.8 | 2.6645 | 1 | 0
BLUEJAY/ACSS | 0.052 | 0.0623 | 563.96 | 31.953 | 2 | 45/7 | 3.9954 | 87 | 603.2246 | 21 | 1867.6 | 2.6645 | 1 | 0
WOOD DUCK/ACSS | 0.0914 | 0.1097 | 306.55 | 25.248 | 2 | 30/7 | 3.6068 | 116 | 378.0638 | 18 | 1408.5 | 3.6068 | 1 | 0
CALUMET/ACSS/TW | 0.0982 | 0.1179 | 286.44 | 21.793 | 2 | 18/7 | 4.5009 | 82 | 333.2251 | 10 | 1063.7 | 2.9134 | 1 | 0
BLUEBIRD/ACSS/TW | 0.0288 | 0.0337 | 1092.45 | 40.843 | 2 | 64/19 | 4.6634 | 187 | 1181.9976 | 22 | 3738.3 | 2.4409 | 1 | 0
CORNCRAKE/ACSS | 0.0601 | 0.0718 | 483.39 | 29.591 | 2 | 20/7 | 19.0297 | 74 | 516.7732 | 13 | 1598.3 | 2.4663 | 1 | 0
BUNTING/ACSS/AW | 0.0482 | 0.0576 | 604.24 | 33.071 | 2 | 45/7 | 4.1351 | 90 | 645.8052 | 21 | 1948.2 | 2.7559 | 1 | 0
ST CROIX/ACSS/TW | 0.0404 | 0.0478 | 743.73 | 32.817 | 2 | 33/7 | 5.3569 | 96 | 782.192 | 15 | 2358.7 | 2.6441 | 1 | 0
DIPPER/ACSS/AW | 0.0429 | 0.0512 | 684.81 | 35.204 | 2 | 45/7 | 4.4018 | 102 | 731.6114 | 21 | 2207.4 | 2.9337 | 1 | 0
TERN/ACSS/TW | 0.0713 | 0.0853 | 402.83 | 24.384 | 2 | 17/7 | 5.494 | 63 | 430.6443 | 9 | 1327.4 | 2.2504 | 1 | 0
CONDOR/ACSS/TW | 0.0706 | 0.0846 | 402.83 | 25.222 | 2 | 20/7 | 5.0648 | 97 | 455.0313 | 12 | 1519.4 | 3.081 | 1 | 0
CONDOR/ACSS/AW | 0.0692 | 0.0853 | 402.83 | 27.737 | 2 | 54/7 | 3.081 | 93 | 455.0313 | 24 | 1459.1 | 3.081 | 1 | 0
BITTERN/ACSS/TW | 0.0458 | 0.0545 | 644.52 | 30.988 | 2 | 35/7 | 4.8412 | 99 | 689.0954 | 16 | 2132.5 | 2.8473 | 1 | 0
BITTERN/ACSS/AW | 0.0454 | 0.0542 | 644.52 | 34.163 | 2 | 45/7 | 4.2697 | 96 | 689.0309 | 21 | 2077.3 | 2.8473 | 1 | 0
WOODCOCK/ACSS | 0.1663 | 0.2 | 170.45 | 17.805 | 2 | 22/7 | 3.142 | 34 | 187.2899 | 14 | 602.6 | 1.745 | 1 | 0
BRANT/ACSS/AW | 0.1368 | 0.1644 | 201.41 | 19.609 | 2 | 24/7 | 3.269 | 46 | 227.4189 | 15 | 729.9 | 2.1793 | 1 | 0
TERN/ACSS/AW | 0.0707 | 0.0853 | 402.83 | 27 | 2 | 45/7 | 3.3757 | 60 | 430.7088 | 21 | 1298.3 | 2.2504 | 1 | 0
BLUEBIRD/ACSS | 0.029 | 0.0338 | 1092.45 | 44.755 | 2 | 84/19 | 4.0691 | 187 | 1181.2234 | 30 | 3736.8 | 2.4409 | 1 | 0
SQUAB/ACSS/AW | 0.0894 | 0.1072 | 306.55 | 24.536 | 2 | 26/7 | 3.8735 | 85 | 356.4509 | 16 | 1177.6 | 3.0124 | 1 | 0
SQUAB/ACSS | 0.0921 | 0.1106 | 306.55 | 24.536 | 2 | 26/7 | 3.8735 | 88 | 356.4509 | 16 | 1237.1 | 3.0124 | 1 | 0
EGRET/ACSS | 0.0871 | 0.1045 | 322.26 | 25.883 | 2 | 30/19 | 3.6982 | 125 | 395.8057 | 18 | 1470.3 | 2.22 | 1 | 0
EGRET/ACSS/AW | 0.0834 | 0.1 | 322.26 | 25.883 | 2 | 30/19 | 3.6982 | 117 | 395.8057 | 18 | 1381.2 | 2.22 | 1 | 0
FALCON/ACSS | 0.037 | 0.045 | 805.65 | 39.243 | 2 | 54/19 | 4.3586 | 189 | 907.7401 | 24 | 3041.8 | 2.667 | 1 | 0
CONDOR/ACSS | 0.0709 | 0.0874 | 402.83 | 27.737 | 2 | 54/7 | 3.081 | 97 | 455.0313 | 24 | 1523.9 | 3.081 | 1 | 0
IBIS/ACSS/AW | 0.1354 | 0.1626 | 201.41 | 19.888 | 2 | 26/7 | 3.1394 | 55 | 234.1931 | 16 | 773.4 | 2.4409 | 1 | 0
FALCON/ACSS/AW | 0.0362 | 0.0439 | 805.65 | 39.243 | 2 | 54/19 | 4.3586 | 183 | 907.7401 | 24 | 2916.8 | 2.667 | 1 | 0
TEAL/ACSS/AW | 0.0877 | 0.1051 | 306.55 | 25.248 | 2 | 30/19 | 3.6068 | 111 | 376.4509 | 18 | 1313.5 | 2.1641 | 1 | 0
SUWANNEE/ACSS/TW | 0.0585 | 0.07 | 486.23 | 28.143 | 2 | 22/7 | 5.3035 | 137 | 565.2892 | 13 | 1961.4 | 3.7922 | 1 | 0
DOVE/ACSS | 0.1 | 0.1201 | 281.98 | 23.546 | 2 | 26/7 | 3.716 | 81 | 327.9348 | 16 | 1139.9 | 3.4595 | 1 | 0
DOVE/ACSS/AW | 0.097 | 0.1164 | 281.98 | 23.546 | 2 | 26/7 | 3.716 | 78 | 327.9348 | 16 | 1084 | 2.8905 | 1 | 0
DOVE/ACSS/TW | 0.0998 | 0.1198 | 281.98 | 21.641 | 2 | 20/7 | 4.2367 | 81 | 327.9348 | 12 | 1137.7 | 2.8905 | 1 | 0
WOODCOCK/ACSS/AW | 0.1632 | 0.1961 | 170.45 | 17.805 | 2 | 22/7 | 3.142 | 32 | 187.2899 | 14 | 582.6 | 1.745 | 1 | 0
STILT/ACSS | 0.0785 | 0.0942 | 362.54 | 26.518 | 2 | 24/7 | 4.3866 | 87 | 409.5476 | 15 | 1372.1 | 2.9235 | 1 | 0
DIPPER/ACSS/TW | 0.0433 | 0.0514 | 684.81 | 31.902 | 2 | 35/7 | 4.9911 | 105 | 732.1276 | 16 | 2265 | 2.9337 | 1 | 0
STARLING/ACSS/AW | 0.0758 | 0.0908 | 362.54 | 26.695 | 2 | 26/7 | 4.2139 | 98 | 421.6121 | 16 | 1393.5 | 3.2766 | 1 | 0
DRAKE/ACSS | 0.0705 | 0.0844 | 402.83 | 28.143 | 2 | 26/7 | 4.4425 | 115 | 468.4507 | 16 | 1628 | 3.4544 | 1 | 0
DRAKE/ACSS/AW | 0.0684 | 0.0819 | 402.83 | 28.143 | 2 | 26/7 | 4.4425 | 109 | 468.4507 | 16 | 1548.9 | 3.4544 | 1 | 0
DRAKE/ACSS/TW | 0.0702 | 0.0842 | 402.83 | 25.654 | 2 | 20/7 | 5.0648 | 115 | 468.4507 | 12 | 1625.1 | 3.4544 | 1 | 0
STARLING/ACSS | 0.0782 | 0.0937 | 362.54 | 26.695 | 2 | 26/7 | 4.2139 | 104 | 421.6121 | 16 | 1465.8 | 3.2766 | 1 | 0
TERN/ACSS | 0.0716 | 0.0864 | 402.83 | 27 | 2 | 45/7 | 3.3757 | 63 | 430.7088 | 21 | 1333.4 | 2.2504 | 1 | 0
STILT/ACSS/AW | 0.0767 | 0.0918 | 362.54 | 26.518 | 2 | 24/7 | 4.3866 | 84 | 409.5476 | 15 | 1314.2 | 2.9235 | 1 | 0
MIRAMICHI/ACSS/TW | 0.0405 | 0.048 | 737.4 | 33.071 | 2 | 36/7 | 5.1079 | 114 | 788.5146 | 16 | 2440.6 | 3.048 | 1 | 0
MARTIN/ACSS/AW | 0.042 | 0.0512 | 684.81 | 36.17 | 2 | 54/19 | 4.0183 | 155 | 771.6114 | 24 | 2478.4 | 2.4105 | 1 | 0
MARTIN/ACSS/TW | 0.0428 | 0.0509 | 684.81 | 33.02 | 2 | 39/19 | 4.7295 | 161 | 771.5468 | 17 | 2580.5 | 2.4105 | 1 | 0
RUDDY/ACSS | 0.0636 | 0.0766 | 456.03 | 28.727 | 2 | 45/7 | 3.5916 | 70 | 487.4184 | 21 | 1510.5 | 2.3952 | 1 | 0
MAUMEE/ACSS/TW | 0.0729 | 0.0874 | 389.25 | 24.816 | 2 | 20/7 | 4.9784 | 93 | 439.9346 | 12 | 1470 | 3.0353 | 1 | 0
GROSBEAK/ACSS | 0.0877 | 0.1053 | 322.26 | 25.146 | 2 | 26/7 | 3.9726 | 93 | 374.7734 | 16 | 1302.1 | 3.0886 | 1 | 0
RAIL/ACSS | 0.0601 | 0.0723 | 483.39 | 29.591 | 2 | 45/7 | 3.6982 | 74 | 516.8377 | 21 | 1599.8 | 3.6982 | 1 | 0
LAPWING/ACSS | 0.0376 | 0.0446 | 805.65 | 38.202 | 2 | 45/7 | 4.7752 | 124 | 861.2886 | 21 | 2666.8 | 3.1826 | 1 | 0
MERRIMACK/ACSS/TW | 0.0405 | 0.0481 | 726.41 | 34.036 | 2 | 39/19 | 4.8692 | 171 | 817.8693 | 17 | 2738.2 | 2.4841 | 1 | 0
MALLARD/ACSS | 0.0699 | 0.0838 | 402.83 | 28.956 | 2 | 30/19 | 4.1351 | 153 | 494.7087 | 18 | 1837.9 | 2.4816 | 1 | 0
MOCKINGBIRD/ACSS | 0.0309 | 0.0361 | 1030.88 | 42.697 | 2 | 72/7 | 4.2697 | 121 | 1075.4817 | 27 | 3213.8 | 2.8473 | 1 | 0
MOCKINGBIRD/ACSS/AW | 0.0307 | 0.0359 | 1030.88 | 42.697 | 2 | 72/7 | 4.2697 | 118 | 1075.4817 | 27 | 3160.7 | 2.8473 | 1 | 0
MOHAWK/ACSS/TW | 0.0976 | 0.1171 | 289.68 | 21.488 | 2 | 18/7 | 4.5263 | 69 | 327.3542 | 10 | 1093.4 | 2.6162 | 1 | 0
PUFFIN/ACSS/TW | 0.0708 | 0.0848 | 402.83 | 24.892 | 2 | 18/7 | 5.3391 | 84 | 446.3862 | 10 | 1451.4 | 2.8143 | 1 | 0
PUFFIN/ACSS | 0.0713 | 0.0854 | 402.83 | 27.356 | 2 | 22/7 | 4.8285 | 79 | 442.3862 | 14 | 1423.3 | 2.6822 | 1 | 0
MYSTIC/ACSS/TW | 0.0838 | 0.1006 | 337.77 | 23.19 | 2 | 20/7 | 4.638 | 81 | 381.5476 | 12 | 1274.3 | 2.8219 | 1 | 0
MERGANSER/ACSS | 0.0585 | 0.0699 | 483.39 | 31.699 | 2 | 30/7 | 4.5339 | 183 | 595.9988 | 18 | 2221.8 | 4.5339 | 1 | 0
RATITE/ACSS/AW | 0.0375 | 0.0442 | 805.65 | 37.897 | 2 | 42/7 | 4.9428 | 101 | 847.3531 | 20 | 2503.7 | 2.7457 | 1 | 0
LAPWING/ACSS/AW | 0.0371 | 0.0441 | 805.65 | 38.202 | 2 | 45/7 | 4.7752 | 120 | 861.2886 | 21 | 2597.9 | 3.1826 | 1 | 0
LAPWING/ACSS/TW | 0.0374 | 0.0442 | 805.65 | 34.493 | 2 | 36/7 | 5.3391 | 124 | 861.3531 | 16 | 2663.8 | 3.1826 | 1 | 0
REDBIRD/ACSS/AW | 0.058 | 0.0693 | 483.39 | 30.378 | 2 | 24/7 | 19.0373 | 109 | 546.1925 | 15 | 1752.2 | 3.3757 | 1 | 0
AVOCET/ACSS/TW | 0.0521 | 0.0621 | 563.96 | 28.677 | 2 | 30/7 | 4.892 | 73 | 592.9666 | 14 | 1787.3 | 2.2962 | 1 | 0
ATHABASKA/ACSS/TW | 0.0314 | 0.0368 | 987.86 | 38.202 | 2 | 42/7 | 5.4737 | 153 | 1056.5785 | 18 | 3272.5 | 3.5357 | 1 | 0
REDBIRD/ACSS | 0.0594 | 0.0711 | 483.39 | 30.378 | 2 | 24/7 | 19.0373 | 116 | 546.1925 | 15 | 1826.7 | 3.3757 | 1 | 0
MARTIN/ACSS | 0.043 | 0.0524 | 684.81 | 36.17 | 2 | 54/19 | 4.0183 | 161 | 771.6114 | 24 | 2584.9 | 2.4105 | 1 | 0
LARK/ACSS/AW | 0.1327 | 0.1593 | 201.41 | 20.472 | 2 | 30/7 | 2.9235 | 74 | 248.3866 | 18 | 869.4 | 2.9235 | 1 | 0
MALLARD/ACSS/AW | 0.067 | 0.0803 | 402.83 | 28.956 | 2 | 30/19 | 4.1351 | 146 | 494.7087 | 18 | 1726.4 | 2.4816 | 1 | 0
LINNET/ACSS | 0.165 | 0.1982 | 170.45 | 18.288 | 2 | 26/7 | 2.888 | 50 | 198.1932 | 16 | 689 | 2.2454 | 1 | 0
LINNET/ACSS/AW | 0.1598 | 0.192 | 170.45 | 18.288 | 2 | 26/7 | 2.888 | 47 | 198.1932 | 16 | 654.5 | 2.2454 | 1 | 0
RATITE/ACSS | 0.0378 | 0.0446 | 805.65 | 37.897 | 2 | 42/7 | 4.9428 | 104 | 847.3531 | 20 | 2553.1 | 2.7457 | 1 | 0
MACAW/ACSS | 0.0719 | 0.0861 | 402.83 | 26.797 | 2 | 42/7 | 3.495 | 52 | 423.6766 | 20 | 1276.2 | 1.9406 | 1 | 0
MACAW/ACSS/AW | 0.0712 | 0.0852 | 402.83 | 26.797 | 2 | 42/7 | 3.495 | 51 | 423.6766 | 20 | 1251.7 | 1.9406 | 1 | 0
MACKENZIE/ACSS/TW | 0.0431 | 0.0511 | 688.96 | 31.979 | 2 | 36/7 | 4.9352 | 106 | 736.6437 | 16 | 2276.9 | 2.9439 | 1 | 0
PTARMIGAN/ACSS | 0.1415 | 0.1701 | 201.41 | 19.101 | 2 | 20/7 | 3.5814 | 32 | 215.4189 | 13 | 666.2 | 1.5926 | 1 | 0
LARK/ACSS | 0.1388 | 0.1666 | 201.41 | 20.472 | 2 | 30/7 | 2.9235 | 78 | 248.3866 | 18 | 927.1 | 2.9235 | 1 | 0
PARTRIDGE/ACSS/AW | 0.2013 | 0.242 | 135.19 | 16.307 | 2 | 26/7 | 2.573 | 37 | 157.161 | 16 | 519.7 | 2.0015 | 1 | 0
PTARMIGAN/ACSS/AW | 0.1413 | 0.1678 | 201.41 | 19.101 | 2 | 20/7 | 3.5814 | 30 | 215.4189 | 13 | 649.6 | 1.5926 | 1 | 0
PARAKEET/ACSS | 0.1005 | 0.1207 | 281.98 | 23.216 | 2 | 24/7 | 3.8684 | 68 | 318.58 | 15 | 1067 | 2.5781 | 1 | 0
PARAKEET/ACSS/AW | 0.0981 | 0.1177 | 281.98 | 23.216 | 2 | 24/7 | 3.8684 | 65 | 318.58 | 15 | 1022.1 | 2.5781 | 1 | 0
PARAKEET/ACSS/TW | 0.1002 | 0.1202 | 281.98 | 21.209 | 2 | 18/7 | 4.4653 | 68 | 318.5155 | 10 | 1063.9 | 2.5781 | 1 | 0
PHOENIX/ACSS/TW | 0.0603 | 0.072 | 483.39 | 26.518 | 2 | 30/7 | 4.5288 | 63 | 508.128 | 14 | 1535.8 | 2.126 | 1 | 0
PARROT/ACSS | 0.0388 | 0.0472 | 765.37 | 38.227 | 2 | 54/19 | 4.2469 | 180 | 861.9338 | 24 | 2887 | 2.5476 | 1 | 0
OXBIRD/ACSS/TW | 0.0488 | 0.0581 | 604.24 | 29.642 | 2 | 30/7 | 5.0648 | 78 | 635.3536 | 14 | 1913.8 | 2.3774 | 1 | 0
PARTRIDGE/ACSS | 0.2077 | 0.2497 | 135.19 | 16.307 | 2 | 26/7 | 2.573 | 40 | 157.161 | 16 | 546 | 2.0015 | 1 | 0
PLATTE/ACSS/TW | 0.0381 | 0.045 | 795.01 | 33.884 | 2 | 33/7 | 5.5372 | 103 | 835.9338 | 15 | 2519.5 | 2.728 | 1 | 0
PHEASANT/ACSS/TW | 0.0452 | 0.0539 | 644.52 | 32.106 | 2 | 39/19 | 4.5872 | 152 | 726.1921 | 17 | 2428.7 | 2.3393 | 1 | 0
PHEASANT/ACSS/AW | 0.0444 | 0.0542 | 644.52 | 35.103 | 2 | 54/19 | 3.8989 | 146 | 726.4502 | 24 | 2333.6 | 2.3393 | 1 | 0
PHEASANT/ACSS | 0.0455 | 0.0556 | 644.52 | 35.103 | 2 | 54/19 | 3.8989 | 152 | 726.4502 | 24 | 2433.1 | 2.3393 | 1 | 0
PEACOCK/ACSS | 0.0926 | 0.1112 | 306.55 | 24.206 | 2 | 24/7 | 4.0335 | 73 | 346.3219 | 15 | 1160.8 | 2.6899 | 1 | 0
PEACOCK/ACSS/AW | 0.0903 | 0.1084 | 306.55 | 24.206 | 2 | 24/7 | 4.0335 | 71 | 346.3219 | 15 | 1111.5 | 2.6899 | 1 | 0
PECOS/ACSS/TW | 0.036 | 0.0428 | 821.87 | 36.17 | 2 | 39/19 | 5.1791 | 200 | 930.9014 | 17 | 3135.6 | 2.7026 | 1 | 0
PEE DEE/ACSS/TW | 0.0342 | 0.0414 | 891.08 | 36.246 | 2 | 37/7 | 4.9962 | 137 | 952.9013 | 17 | 2949.5 | 3.3503 | 1 | 0
PARROT/ACSS/AW | 0.038 | 0.0461 | 765.37 | 38.227 | 2 | 54/19 | 4.2469 | 173 | 861.9338 | 24 | 2768.4 | 2.5476 | 1 | 0
ORTOLAN/ACSS/AW | 0.0551 | 0.0661 | 523.67 | 30.785 | 2 | 45/7 | 3.8481 | 78 | 559.5473 | 21 | 1687.1 | 2.5654 | 1 | 0
RAIL/ACSS/TW | 0.0601 | 0.0718 | 483.39 | 26.949 | 2 | 32/7 | 4.3866 | 74 | 516.8377 | 14 | 1599.8 | 2.4663 | 1 | 0
NUTHATCH/ACSS | 0.0393 | 0.0467 | 765.37 | 37.211 | 2 | 45/7 | 4.6533 | 118 | 818.0629 | 21 | 2534.3 | 3.1013 | 1 | 0
NUTHATCH/ACSS/AW | 0.0388 | 0.0462 | 765.37 | 37.211 | 2 | 45/7 | 4.6533 | 114 | 818.0629 | 21 | 2466.8 | 3.1013 | 1 | 0
POWDER/ACSS/TW | 0.0288 | 0.0337 | 1091.33 | 40.691 | 2 | 64/19 | 4.6584 | 187 | 1179.9976 | 22 | 3717.4 | 2.4409 | 1 | 0
POTOMAC/ACSS/TW | 0.0381 | 0.0451 | 789.13 | 34.163 | 2 | 36/7 | 5.2832 | 121 | 843.8048 | 16 | 2611.7 | 3.1521 | 1 | 0
ORIOLE/ACSS | 0.1639 | 0.1968 | 170.45 | 18.821 | 2 | 30/7 | 2.6899 | 66 | 210.2576 | 18 | 784.3 | 2.6899 | 1 | 0
PIPER/ACSS | 0.1837 | 0.2206 | 152.01 | 17.78 | 2 | 30/7 | 2.54 | 59 | 187.0319 | 18 | 699.4 | 2.54 | 1 | 0
ORTOLAN/ACSS | 0.0557 | 0.0669 | 523.67 | 30.785 | 2 | 45/7 | 3.8481 | 81 | 559.5473 | 21 | 1732.2 | 2.5654 | 1 | 0
NELSON/ACSS/TW | 0.0463 | 0.0551 | 636.97 | 30.81 | 2 | 35/7 | 4.8133 | 98 | 681.0954 | 16 | 2108.7 | 2.8321 | 1 | 0
ORTOLAN/ACSS/TW | 0.0557 | 0.0664 | 523.67 | 27.991 | 2 | 32/7 | 4.5644 | 81 | 559.5473 | 14 | 1733.7 | 2.5654 | 1 | 0
PLOVER/ACSS/TW | 0.0405 | 0.0482 | 725.09 | 33.96 | 2 | 37/19 | 4.9962 | 171 | 817.0306 | 17 | 2729.3 | 2.4816 | 1 | 0
PLOVER/ACSS/AW | 0.0398 | 0.0485 | 725.09 | 37.211 | 2 | 54/19 | 4.1351 | 164 | 817.4177 | 24 | 2625.1 | 2.4816 | 1 | 0
PLOVER/ACSS | 0.0408 | 0.0496 | 725.09 | 37.211 | 2 | 54/19 | 4.1351 | 171 | 817.4177 | 24 | 2738.2 | 2.4816 | 1 | 0
OSTRICH/ACSS | 0.1849 | 0.2221 | 152.01 | 17.272 | 2 | 26/7 | 2.728 | 44 | 177.0319 | 16 | 614.6 | 2.1209 | 1 | 0
OSTRICH/ACSS/AW | 0.1791 | 0.2152 | 152.01 | 17.272 | 2 | 26/7 | 2.728 | 42 | 177.0319 | 16 | 584.1 | 2.1209 | 1 | 0
OSWEGO/ACSS/TW | 0.0837 | 0.1005 | 336.85 | 23.546 | 2 | 20/7 | 4.6304 | 97 | 391.7412 | 12 | 1359.3 | 3.1598 | 1 | 0
ORIOLE/ACSS/AW | 0.1566 | 0.1882 | 170.45 | 18.821 | 2 | 30/7 | 2.6899 | 63 | 210.2576 | 18 | 736 | 2.6899 | 1 | 0
HEN/ACSS/AW | 0.1107 | 0.1329 | 241.7 | 22.428 | 2 | 30/7 | 3.2029 | 89 | 298.0639 | 18 | 1043.5 | 3.2029 | 1 | 0
JOREE/ACSS/AW | 0.0258 | 0.0298 | 1274.35 | 47.752 | 2 | 76/19 | 4.6203 | 165 | 1343.6102 | 28 | 4002.1 | 2.1565 | 1 | 0
ROADRUNNER/ACSS/AW | 0.0302 | 0.0353 | 1042.28 | 43.18 | 2 | 76/19 | 4.1783 | 135 | 1098.8365 | 28 | 3273.2 | 1.9507 | 1 | 0
ROOK/ACSS/TW | 0.0878 | 0.1054 | 322.26 | 22.606 | 2 | 19/7 | 4.6482 | 77 | 364.0638 | 11 | 1214.3 | 2.7559 | 1 | 0
JUNCO/ACSS/AW | 0.1973 | 0.2371 | 135.19 | 16.764 | 2 | 30/7 | 2.3952 | 50 | 135.161 | 18 | 582.6 | 2.3952 | 1 | 0
ROOK/ACSS/AW | 0.086 | 0.1031 | 322.26 | 24.816 | 2 | 24/7 | 4.1351 | 74 | 364.0638 | 15 | 1167.9 | 2.7559 | 1 | 0
HAWK/ACSS/TW | 0.1162 | 0.1396 | 241.7 | 20.041 | 2 | 18/7 | 4.1351 | 69 | 281.0317 | 10 | 974.7 | 2.6746 | 1 | 0
RIO GRANDE/ACSS/TW | 0.038 | 0.0451 | 776.92 | 35.103 | 2 | 39/19 | 5.0368 | 183 | 875.5466 | 17 | 2928.7 | 2.5705 | 1 | 0
JUNCO/ACSS | 0.2001 | 0.248 | 135.19 | 16.764 | 2 | 30/7 | 2.3952 | 52 | 135.161 | 18 | 620.3 | 2.3952 | 1 | 0
ROADRUNNER/ACSS | 0.0304 | 0.0356 | 1042.28 | 43.18 | 2 | 76/19 | 4.1783 | 141 | 1098.8365 | 28 | 3341.1 | 1.9507 | 1 | 0
KETTLE/ACSS/TW | 0.0599 | 0.0716 | 485.01 | 26.924 | 2 | 32/7 | 4.3942 | 75 | 518.5796 | 14 | 1605.7 | 2.4714 | 1 | 0
HUDSON/ACSS/TW | 0.0491 | 0.0586 | 586.96 | 30.378 | 2 | 26/7 | 5.3619 | 138 | 663.289 | 16 | 2215.9 | 3.7262 | 1 | 0
JAMES/ACSS/TW | 0.0341 | 0.0403 | 876.9 | 37.338 | 2 | 34/19 | 5.7302 | 206 | 987.998 | 14 | 3305.2 | 2.7305 | 1 | 0
IBIS/ACSS | 0.1397 | 0.1678 | 201.41 | 19.888 | 2 | 26/7 | 3.1394 | 58 | 234.1931 | 16 | 814 | 2.4409 | 1 | 0
ROOK/ACSS | 0.0882 | 0.1058 | 322.26 | 24.816 | 2 | 24/7 | 4.1351 | 77 | 364.0638 | 15 | 1218.8 | 2.7559 | 1 | 0
HEN/ACSS | 0.1158 | 0.1389 | 241.7 | 22.428 | 2 | 30/7 | 3.2029 | 93 | 298.0639 | 18 | 1111.7 | 3.2029 | 1 | 0
KIWI/ACSS | 0.0294 | 0.0342 | 1098.02 | 44.069 | 2 | 72/7 | 4.4069 | 129 | 1145.6751 | 27 | 3423.7 | 2.9388 | 1 | 0
HAWK/ACSS/AW | 0.113 | 0.1356 | 241.7 | 21.793 | 2 | 26/7 | 3.4392 | 66 | 281.0317 | 16 | 928.5 | 2.6746 | 1 | 0
RAIL/ACSS/AW | 0.0594 | 0.0714 | 483.39 | 29.591 | 2 | 45/7 | 3.6982 | 72 | 516.8377 | 21 | 1558.4 | 3.6982 | 1 | 0
JOREE/ACSS | 0.026 | 0.0301 | 1274.35 | 47.752 | 2 | 76/19 | 4.6203 | 172 | 1343.6102 | 28 | 4085 | 2.1565 | 1 | 0
BALDPATE/ACSS | 0.062 | 0.0743 | 456.03 | 30.785 | 2 | 30/7 | 4.3993 | 172 | 561.9989 | 18 | 2098.3 | 4.3993 | 1 | 0
REDWING/ACSS | 0.0775 | 0.093 | 362.54 | 27.457 | 2 | 30/19 | 3.9218 | 137 | 445.2249 | 18 | 1653.3 | 2.352 | 1 | 0
REDWING/ACSS/AW | 0.0743 | 0.0891 | 362.54 | 27.457 | 2 | 30/19 | 3.9218 | 131 | 445.2249 | 18 | 1552.3 | 2.352 | 1 | 0
KIWI/ACSS/AW | 0.0292 | 0.034 | 1098.02 | 44.069 | 2 | 72/7 | 4.4069 | 125 | 1145.6751 | 27 | 3367 | 2.9388 | 1 | 0
HAWK/ACSS | 0.1166 | 0.14 | 241.7 | 21.793 | 2 | 26/7 | 3.4392 | 69 | 281.0317 | 16 | 977.7 | 2.6746 | 1 | 0
PLUTO | 0.1673 | 0.168 | 206 | 18.796 | 4 | 19/0 | 3.749 | 32 | 209.806 | 19 | 578 | 9999 | 1 | 0
TULIP/T2 | 0.0874 | 0.1041 | 340.91 | 27.686 | 4 | 19/0 | 3.3807 | 55 | 340.9025 | 12 | 939.9 | 9999 | 1 | 0
NEPTUNE | 0.2236 | 0.224 | 155 | 16.307 | 4 | 19/0 | 3.2512 | 25 | 157.6126 | 19 | 433 | 9999 | 1 | 0
VIRGO | 0.0244 | 0.0273 | 1409.97 | 49.505 | 4 | 91/0 | 4.5009 | 207 | 1447.0294 | 91 | 4010 | 9999 | 1 | 0
CAMELLIA | 0.0599 | 0.0708 | 506.7 | 29.261 | 4 | 61/0 | 3.2512 | 79 | 506.3861 | 24 | 1396.2 | 9999 | 1 | 0
IRIS | 0.8712 | 1.0439 | 33.62 | 7.417 | 4 | 7/0 | 2.474 | 6 | 33.6774 | 6 | 92.7 | 9999 | 1 | 0
GEMINI | 2.089 | 2.0899 | 16.6 | 5.258 | 4 | 7/0 | 1.7501 | 3 | 16.8387 | 7 | 46.1 | 9999 | 1 | 0
CANNA | 0.146 | 0.1752 | 201.41 | 18.364 | 4 | 19/0 | 3.6754 | 32 | 201.548 | 12 | 555.7 | 9999 | 1 | 0
CANNA/T2 | 0.0744 | 0.0885 | 402.83 | 30.099 | 4 | 19/0 | 3.6754 | 63 | 402.8379 | 12 | 1110.9 | 9999 | 1 | 0
CROCUS | 0.0677 | 0.0808 | 443.11 | 27.381 | 4 | 61/0 | 3.0429 | 70 | 443.612 | 24 | 1221.8 | 9999 | 1 | 0
TULIP | 0.1727 | 0.2063 | 170.45 | 16.916 | 4 | 19/0 | 3.3807 | 27 | 170.5803 | 12 | 470.3 | 9999 | 1 | 0
GOLDENTUFT | 0.1292 | 0.1547 | 228.02 | 19.533 | 4 | 19/0 | 3.9091 | 35 | 227.9995 | 12 | 628.6 | 9999 | 1 | 0
URANUS | 0.0699 | 0.0711 | 492.99 | 29.312 | 4 | 61/0 | 3.2512 | 75 | 505.999 | 61 | 1400 | 9999 | 1 | 0
GOLDENROD | 0.0628 | 0.0739 | 483.39 | 28.6 | 4 | 61/0 | 3.1775 | 75 | 483.741 | 24 | 1333.5 | 9999 | 1 | 0
POPPY | 0.548 | 0.6568 | 53.51 | 9.347 | 4 | 7/0 | 3.1191 | 9 | 53.4838 | 6 | 147.5 | 9999 | 1 | 0
ORCHID | 0.0926 | 0.11 | 322.26 | 23.317 | 4 | 37/0 | 3.3299 | 51 | 322.2574 | 18 | 888.3 | 9999 | 1 | 0
VIOLET | 0.082 | 0.0982 | 362.54 | 24.74 | 4 | 37/0 | 3.5331 | 57 | 362.709 | 18 | 1000 | 9999 | 1 | 0
VERBENA | 0.0839 | 0.1 | 354.69 | 24.435 | 4 | 37/0 | 3.4925 | 56 | 354.4509 | 18 | 977.1 | 9999 | 1 | 0
POPPY/T2 | 0.2745 | 0.3287 | 107.02 | 15.291 | 4 | 7/0 | 3.1191 | 18 | 106.9675 | 6 | 294.8 | 9999 | 1 | 0
GLADIOLUS | 0.0412 | 0.0483 | 765.62 | 35.992 | 4 | 61/0 | 3.998 | 114 | 765.8049 | 24 | 2111.7 | 9999 | 1 | 0
IRIS/T2 | 0.4363 | 0.5226 | 67.24 | 12.141 | 4 | 7/0 | 2.474 | 12 | 67.2257 | 6 | 185.3 | 9999 | 1 | 0
VALERIAN | 0.2318 | 0.2778 | 126.68 | 14.554 | 4 | 19/0 | 2.9134 | 21 | 126.6449 | 12 | 349.1 | 9999 | 1 | 0
VENUS | 0.0524 | 0.054 | 658.99 | 33.807 | 4 | 61/0 | 3.749 | 98 | 673.6761 | 24 | 1860.1 | 9999 | 1 | 0
VENUS | 0.0524 | 0.054 | 658.99 | 33.807 | 4 | 61/0 | 3.749 | 98 | 673.6761 | 61 | 1860 | 9999 | 1 | 0
BUTTERFLY | 0.1091 | 0.116 | 311.39 | 23.241 | 4 | 19/0 | 4.6507 | 48 | 322.3865 | 12 | 887.4 | 9999 | 1 | 0
GRUB | 0.7061 | 0.708 | 48.9 | 8.992 | 4 | 7/0 | 2.9997 | 8 | 49.4193 | 7 | 134.8 | 9999 | 1 | 0
HYACINTH | 0.1168 | 0.1398 | 253.35 | 20.65 | 4 | 37/0 | 2.9515 | 41 | 253.1608 | 18 | 697.9 | 9999 | 1 | 0
ROSE | 1.3869 | 1.6615 | 21.15 | 5.893 | 4 | 7/0 | 1.9609 | 4 | 21.1612 | 7 | 58.3 | 9999 | 1 | 0
TRITON | 0.0862 | 0.0873 | 399.99 | 26.289 | 4 | 37/0 | 3.749 | 63 | 408.7089 | 18 | 1130 | 9999 | 1 | 0
PHLOX/T2 | 0.1731 | 0.2071 | 170.05 | 19.304 | 4 | 7/0 | 3.9319 | 27 | 170.0642 | 6 | 468.5 | 9999 | 1 | 0
PHLOX | 0.3455 | 0.4132 | 85.02 | 11.786 | 4 | 7/0 | 3.9319 | 14 | 84.9676 | 6 | 234.4 | 9999 | 1 | 0
ROSE/T2 | 0.693 | 0.7616 | 42.31 | 9.652 | 4 | 7/0 | 1.9609 | 8 | 42.3225 | 6 | 116.5 | 9999 | 1 | 0
CICADA | 0.0562 | 0.0279 | 601.59 | 32.537 | 4 | 37/0 | 4.6507 | 90 | 627.8052 | 18 | 1734.3 | 9999 | 1 | 0
PETUNIA | 0.0789 | 0.0938 | 380.03 | 25.324 | 4 | 37/0 | 3.617 | 58 | 380.1283 | 18 | 1048.1 | 9999 | 1 | 0
HAWTHORN | 0.0509 | 0.0601 | 604.24 | 31.953 | 4 | 61/0 | 3.5509 | 94 | 604.0633 | 24 | 1665.3 | 9999 | 1 | 0
CHAFER | 0.1649 | 0.168 | 206.5 | 18.923 | 4 | 19/0 | 3.7795 | 33 | 213.806 | 12 | 588.6 | 9999 | 1 | 0
CENTIPEDE | 0.0846 | 0.0848 | 398.99 | 26.492 | 4 | 37/0 | 3.7795 | 62 | 416.3217 | 18 | 1149.8 | 9999 | 1 | 0
CATTAIL | 0.0789 | 0.0938 | 380.03 | 25.349 | 4 | 61/0 | 2.8169 | 60 | 380.1283 | 24 | 1048 | 9999 | 1 | 0
PEONY | 0.1932 | 0.2311 | 152.01 | 15.977 | 4 | 19/0 | 3.1928 | 24 | 152.1287 | 12 | 419.4 | 9999 | 1 | 0
CARNATION | 0.0432 | 0.0508 | 725.09 | 35.027 | 4 | 61/0 | 3.8913 | 108 | 725.1598 | 24 | 2000.1 | 9999 | 1 | 0
TRILLIUM | 0.0244 | 0.0277 | 1520.1 | 50.749 | 4 | 127/0 | 3.904 | 224 | 1519.997 | 36 | 4232.3 | 9999 | 1 | 0
PEACHBELL | 2.2065 | 2.6439 | 13.3 | 4.674 | 4 | 7/0 | 1.5545 | 3 | 13.2903 | 6 | 36.6 | 9999 | 1 | 0
OXLIP | 0.274 | 0.3281 | 107.22 | 13.259 | 4 | 7/0 | 4.4171 | 17 | 107.2901 | 6 | 295.7 | 9999 | 1 | 0
ZINNIA | 0.1168 | 0.1398 | 253.35 | 20.599 | 4 | 19/0 | 4.1199 | 39 | 253.2898 | 12 | 698.2 | 9999 | 1 | 0
COWSLIP | 0.0326 | 0.0378 | 1013.4 | 41.427 | 4 | 91/0 | 3.7643 | 152 | 1012.9012 | 30 | 2791.8 | 9999 | 1 | 0
COSMOS/T2 | 0.0626 | 0.0743 | 483.39 | 32.969 | 4 | 19/0 | 4.0234 | 74 | 483.3539 | 12 | 1331.3 | 9999 | 1 | 0
COSMOS | 0.1224 | 0.146 | 241.7 | 20.142 | 4 | 19/0 | 4.0234 | 37 | 241.5479 | 12 | 666 | 9999 | 1 | 0
SCORPION | 0.0667 | 0.0604 | 507.19 | 29.87 | 4 | 37/0 | 4.2697 | 77 | 529.2247 | 18 | 1461.8 | 9999 | 1 | 0
SATURN | 0.1344 | 0.135 | 255.99 | 21.006 | 4 | 37/0 | 2.9997 | 42 | 261.4833 | 37 | 721 | 9999 | 1 | 0
HAWKWEED | 0.0598 | 0.0708 | 506.7 | 29.235 | 4 | 37/0 | 4.1758 | 77 | 506.7087 | 18 | 1396.9 | 9999 | 1 | 0
HORNET | 0.2236 | 0.225 | 152.4 | 16.256 | 4 | 19/0 | 3.2512 | 25 | 157.7416 | 12 | 433.9 | 9999 | 1 | 0
TAURUS | 0.1047 | 0.106 | 331 | 23.8 | 4 | 19/0 | 4.7498 | 51 | 336.709 | 19 | 926 | 9999 | 1 | 0
OXLIP/T2 | 0.1376 | 0.1645 | 214.44 | 21.717 | 4 | 7/0 | 4.4171 | 34 | 214.4512 | 6 | 591.1 | 9999 | 1 | 0
PANSY | 0.6922 | 0.8289 | 42.41 | 8.331 | 4 | 7/0 | 2.7762 | 7 | 42.387 | 6 | 116.8 | 9999 | 1 | 0
PANSY/T2 | 0.3462 | 0.4146 | 84.82 | 13.64 | 4 | 7/0 | 2.7762 | 15 | 84.774 | 6 | 233.5 | 9999 | 1 | 0
COLUMBINE | 0.0454 | 0.0535 | 684.81 | 34.036 | 4 | 61/0 | 3.7821 | 104 | 685.1599 | 24 | 1888.5 | 9999 | 1 | 0
COCKSCOMB | 0.0659 | 0.0783 | 456.03 | 27.737 | 4 | 37/0 | 3.9624 | 69 | 456.2572 | 18 | 1257.8 | 9999 | 1 | 0
COCKROACH | 0.1319 | 0.143 | 256.29 | 21.082 | 4 | 19/0 | 4.2189 | 41 | 265.2898 | 12 | 730.2 | 9999 | 1 | 0
COREOPSIS | 0.0394 | 0.0462 | 805.65 | 36.932 | 4 | 61/0 | 4.1021 | 120 | 806.45 | 24 | 2221.8 | 9999 | 1 | 0
DAHLIA/T2 | 0.0542 | 0.0641 | 563.96 | 35.585 | 4 | 19/0 | 4.3459 | 87 | 563.9989 | 12 | 1553.3 | 9999 | 1 | 0
LIBRA | 0.7073 | 0.708 | 48.8 | 8.992 | 4 | 7/0 | 2.9997 | 8 | 49.4838 | 7 | 135 | 9999 | 1 | 0
SNAPDRAGON | 0.0659 | 0.0783 | 456.03 | 27.788 | 4 | 61/0 | 3.0861 | 71 | 456.2572 | 24 | 1257.9 | 9999 | 1 | 0
FLY | 0.5485 | 0.588 | 63 | 10.211 | 4 | 7/0 | 3.4011 | 10 | 63.6773 | 7 | 174.1 | 9999 | 1 | 0
DAISY/T2 | 0.1095 | 0.1308 | 270.38 | 24.359 | 4 | 7/0 | 4.9606 | 43 | 270.322 | 6 | 745.6 | 9999 | 1 | 0
MEADOWSWEET | 0.0976 | 0.1168 | 304.02 | 22.631 | 4 | 37/0 | 3.2334 | 48 | 303.8058 | 18 | 837.5 | 9999 | 1 | 0
SNEEZEWORT | 0.2318 | 0.2778 | 126.68 | 14.402 | 4 | 7/0 | 4.8006 | 20 | 126.7094 | 6 | 349.3 | 9999 | 1 | 0
LILAC | 0.0746 | 0.0882 | 402.83 | 26.111 | 4 | 61/0 | 2.9007 | 64 | 403.096 | 24 | 1111.2 | 9999 | 1 | 0
JUPITER | 1.2583 | 1.26 | 27.5 | 6.756 | 4 | 7/0 | 2.2504 | 5 | 27.8064 | 7 | 75.9 | 9999 | 1 | 0
LILY/T2 | 0.5497 | 0.6583 | 53.3 | 10.82 | 4 | 7/0 | 2.2022 | 10 | 53.3547 | 6 | 146.9 | 9999 | 1 | 0
BLUEBELL | 0.058 | 0.069 | 523.67 | 29.718 | 4 | 37/0 | 4.2469 | 79 | 524.128 | 18 | 1444.9 | 9999 | 1 | 0
SYRINGA | 0.1224 | 0.146 | 241.7 | 20.193 | 4 | 37/0 | 2.8829 | 39 | 241.4834 | 18 | 665.8 | 9999 | 1 | 0
DAHLIA | 0.105 | 0.1255 | 281.98 | 21.717 | 4 | 19/0 | 4.3459 | 43 | 281.8704 | 12 | 777 | 9999 | 1 | 0
MERCURY | 0.3152 | 0.315 | 110 | 13.487 | 4 | 7/0 | 4.5009 | 17 | 111.2901 | 7 | 305 | 9999 | 1 | 0
DAISY | 0.2175 | 0.2604 | 135.19 | 14.884 | 4 | 7/0 | 4.9606 | 21 | 135.2901 | 6 | 372.9 | 9999 | 1 | 0
FLAG | 0.0839 | 0.1 | 354.69 | 24.486 | 4 | 61/0 | 2.7203 | 57 | 354.5154 | 24 | 977.4 | 9999 | 1 | 0
VIRGO | 0.0244 | 0.0273 | 1409.97 | 49.505 | 4 | 91/0 | 4.5009 | 207 | 1447.0294 | 30 | 4010 | 9999 | 1 | 0
MARS | 0.452 | 0.452 | 76.3 | 11.303 | 4 | 7/0 | 3.749 | 12 | 77.2902 | 7 | 212 | 9999 | 1 | 0
MARIGOLD | 0.0542 | 0.064 | 563.96 | 30.886 | 4 | 61/0 | 3.4315 | 88 | 564.1279 | 24 | 1555.1 | 9999 | 1 | 0
ANEMONE | 0.0677 | 0.0808 | 443.11 | 27.356 | 4 | 37/0 | 3.9065 | 67 | 443.483 | 18 | 1221.8 | 9999 | 1 | 0
MAGNOLIA | 0.0628 | 0.0746 | 483.39 | 28.55 | 4 | 37/0 | 4.0792 | 73 | 483.5474 | 18 | 1333.1 | 9999 | 1 | 0
ARBUTUS | 0.0746 | 0.0882 | 402.83 | 26.06 | 4 | 37/0 | 3.7236 | 62 | 402.9024 | 18 | 1110.8 | 9999 | 1 | 0
ASTER | 0.435 | 0.5207 | 67.44 | 10.516 | 4 | 7/0 | 3.5027 | 11 | 67.4192 | 6 | 185.9 | 9999 | 1 | 0
LUPINE | 0.0277 | 0.0318 | 1266.75 | 46.304 | 4 | 91/0 | 4.2088 | 186 | 1265.8039 | 30 | 3524 | 9999 | 1 | 0
DAFFODIL | 0.1659 | 0.1988 | 177.35 | 17.247 | 4 | 19/0 | 3.4468 | 28 | 177.29 | 12 | 488.7 | 9999 | 1 | 0
JEWELWEED | 0.0326 | 0.0378 | 1013.4 | 41.402 | 4 | 61/0 | 4.5999 | 152 | 1013.5464 | 24 | 2791.8 | 9999 | 1 | 0
WASP | 0.3286 | 0.342 | 105.2 | 13.183 | 4 | 7/0 | 4.3891 | 16 | 106.1933 | 7 | 290 | 9999 | 1 | 0
NASTURTIUM | 0.0826 | 0.0982 | 362.54 | 24.765 | 4 | 61/0 | 2.7508 | 58 | 362.5154 | 24 | 999.4 | 9999 | 1 | 0
NARCISSUS | 0.048 | 0.0566 | 644.52 | 33.02 | 4 | 61/0 | 3.6678 | 98 | 644.5148 | 24 | 1776.9 | 9999 | 1 | 0
MOON | 0.2834 | 0.284 | 122 | 14.3 | 4 | 7/0 | 4.7498 | 19 | 123.9998 | 7 | 340 | 9999 | 1 | 0
JESSAMINE | 0.0364 | 0.0424 | 886.73 | 38.735 | 4 | 61/0 | 4.3028 | 132 | 887.095 | 24 | 2445 | 9999 | 1 | 0
LEO | 1.0176 | 1.02 | 33.9 | 7.493 | 4 | 7/0 | 2.4994 | 6 | 34.387 | 7 | 94.3 | 9999 | 1 | 0
BLUEBONNET | 0.0222 | 0.025 | 1773.45 | 54.813 | 4 | 127/0 | 4.2164 | 261 | 1773.5448 | 36 | 4985.3 | 9999 | 1 | 0
ASTER/T2 | 0.218 | 0.2609 | 134.88 | 17.221 | 4 | 7/0 | 3.5027 | 22 | 134.8384 | 6 | 371.7 | 9999 | 1 | 0
MISTLETOE | 0.105 | 0.1255 | 281.98 | 21.793 | 4 | 37/0 | 3.114 | 44 | 281.8059 | 18 | 776.8 | 9999 | 1 | 0
LAUREL | 0.2175 | 0.2604 | 135.19 | 15.062 | 4 | 19/0 | 3.0099 | 22 | 135.161 | 12 | 372.6 | 9999 | 1 | 0
LARKSPUR | 0.058 | 0.069 | 523.67 | 29.769 | 4 | 61/0 | 3.3071 | 81 | 523.999 | 24 | 1444.4 | 9999 | 1 | 0
KAYAK | 0.425 | 9999 | 78.54 | 11.354 | 5 | 7/0 | 3.7846 | 19 | 78.774 | 6 | 217.1 | 9999 | 1 | 0
KIBE | 0.5356 | 9999 | 62.32 | 10.109 | 5 | 7/0 | 3.3706 | 15 | 62.4515 | 6 | 172.2 | 9999 | 1 | 0
RATCH | 0.2349 | 9999 | 142.38 | 15.443 | 5 | 19/0 | 3.0937 | 34 | 142.5804 | 12 | 393.2 | 9999 | 1 | 0
KOPECK | 0.338 | 9999 | 99.31 | 12.751 | 5 | 7/0 | 4.2469 | 22 | 99.1611 | 6 | 273.4 | 9999 | 1 | 0
KENCH | 0.8513 | 9999 | 39.02 | 8.026 | 5 | 7/0 | 2.6721 | 10 | 39.2257 | 6 | 108.2 | 9999 | 1 | 0
REX | 0.1317 | 9999 | 255.38 | 20.676 | 5 | 19/0 | 4.1351 | 56 | 255.1608 | 12 | 703.5 | 9999 | 1 | 0
REMEX | 0.1193 | 9999 | 283.25 | 21.793 | 5 | 19/0 | 4.3586 | 62 | 283.4833 | 12 | 781.6 | 9999 | 1 | 0
RADIAN | 0.1678 | 9999 | 200.15 | 18.313 | 5 | 19/0 | 3.6627 | 47 | 199.9351 | 12 | 551.1 | 9999 | 1 | 0
RAGOUT | 0.1429 | 9999 | 235.62 | 19.863 | 5 | 19/0 | 3.9776 | 54 | 235.806 | 12 | 650.2 | 9999 | 1 | 0
KAZOO | 2.1562 | 9999 | 15.71 | 5.029 | 5 | 7/0 | 1.6789 | 4 | 15.4838 | 6 | 42.7 | 9999 | 1 | 0
RAMIE | 0.2119 | 9999 | 158.6 | 16.307 | 5 | 19/0 | 3.2614 | 38 | 158.4513 | 12 | 436.9 | 9999 | 1 | 0
KAKI | 1.3546 | 9999 | 24.83 | 6.35 | 5 | 7/0 | 2.1184 | 6 | 24.6451 | 6 | 68 | 9999 | 1 | 0
SOLAR | 0.0727 | 9999 | 469.71 | 28.143 | 5 | 37/0 | 4.0208 | 106 | 469.8055 | 18 | 1295.3 | 9999 | 1 | 0
RUBLE | 0.1137 | 9999 | 297.43 | 22.327 | 5 | 19/0 | 4.4653 | 65 | 297.5478 | 12 | 820.3 | 9999 | 1 | 0
RADAR | 0.1864 | 9999 | 179.88 | 17.348 | 5 | 19/0 | 3.4747 | 43 | 179.9351 | 12 | 496 | 9999 | 1 | 0
KITTLE | 0.2678 | 9999 | 125.15 | 14.3 | 5 | 7/0 | 4.7701 | 28 | 125.0965 | 6 | 345 | 9999 | 1 | 0
REDE | 0.1578 | 9999 | 212.81 | 18.872 | 5 | 19/0 | 3.7744 | 50 | 212.5802 | 12 | 586.2 | 9999 | 1 | 0
RUNE | 0.1025 | 9999 | 330.37 | 23.52 | 5 | 19/0 | 4.7092 | 72 | 330.58 | 12 | 911.3 | 9999 | 1 | 0
SPAR | 0.0907 | 9999 | 375.46 | 25.146 | 5 | 37/0 | 3.5966 | 86 | 375.3541 | 18 | 1034.9 | 9999 | 1 | 0
AGATE | 2.36 | 2.3599 | 14.3 | 5.258 | 6 | 7/0 | 1.7501 | 5 | 16.8387 | 6 | 46.1 | 9999 | 1 | 0
AZUSA | 0.5456 | 0.6388 | 62.32 | 10.109 | 6 | 7/0 | 3.3706 | 20 | 62.4515 | 6 | 172.2 | 9999 | 1 | 0
SPINEL | 0.0793 | 0.0804 | 426.99 | 29.312 | 6 | 61/0 | 3.2512 | 135 | 505.999 | 24 | 1400.1 | 9999 | 1 | 0
TOPAZ | 0.0597 | 0.061 | 568.99 | 33.807 | 6 | 61/0 | 3.749 | 179 | 673.6761 | 24 | 1860.1 | 9999 | 1 | 0
CANTON | 0.1715 | 0.2001 | 200.15 | 18.313 | 6 | 19/0 | 3.6601 | 59 | 199.9351 | 12 | 551.1 | 9999 | 1 | 0
RUBY | 0.1534 | 0.153 | 221 | 21.006 | 6 | 37/0 | 2.9997 | 73 | 261.4833 | 18 | 721 | 9999 | 1 | 0
ELGIN | 0.1044 | 0.1218 | 330.37 | 23.52 | 6 | 19/0 | 4.7066 | 97 | 330.58 | 12 | 911.3 | 9999 | 1 | 0
PEARL | 0.1904 | 0.19 | 178 | 18.796 | 6 | 19/0 | 3.749 | 59 | 209.806 | 12 | 576.1 | 9999 | 1 | 0
EMERALD | 0.8038 | 0.804 | 42.1 | 8.992 | 6 | 7/0 | 2.9997 | 14 | 49.4838 | 6 | 135 | 9999 | 1 | 0
RUTILE | 0.1187 | 0.12 | 284.99 | 23.8 | 6 | 19/0 | 4.7498 | 94 | 336.709 | 12 | 924 | 9999 | 1 | 0
ALTON | 1.3794 | 1.6156 | 24.83 | 6.35 | 6 | 7/0 | 2.1184 | 8 | 24.6451 | 6 | 68 | 9999 | 1 | 0
OPAL | 0.254 | 0.254 | 134 | 16.307 | 6 | 19/0 | 3.2512 | 44 | 157.6126 | 12 | 433.1 | 9999 | 1 | 0
AMES | 0.8699 | 1.019 | 39.02 | 8.026 | 6 | 7/0 | 2.6721 | 12 | 39.2257 | 6 | 108.2 | 9999 | 1 | 0
AMETHYST | 1.4256 | 1.43 | 23.7 | 6.756 | 6 | 7/0 | 2.2504 | 8 | 27.8064 | 6 | 75.9 | 9999 | 1 | 0
JADE | 0.357 | 0.357 | 94.8 | 13.487 | 6 | 7/0 | 4.5009 | 31 | 111.2901 | 6 | 304 | 9999 | 1 | 0
DIAMOND | 1.1584 | 1.16 | 29.3 | 7.493 | 6 | 7/0 | 2.4994 | 10 | 34.387 | 6 | 94.3 | 9999 | 1 | 0
JASPER | 0.3211 | 0.321 | 106 | 14.3 | 6 | 7/0 | 4.7498 | 35 | 123.9998 | 6 | 339 | 9999 | 1 | 0
GARNET | 0.5151 | 0.515 | 65.8 | 11.303 | 6 | 7/0 | 3.749 | 22 | 77.2902 | 6 | 211 | 9999 | 1 | 0
CAIRO | 0.1454 | 0.1696 | 235.62 | 19.863 | 6 | 19/0 | 3.9751 | 69 | 235.806 | 12 | 650.2 | 9999 | 1 | 0
ZIRCON | 0.0278 | 0.0305 | 1219.98 | 49.505 | 6 | 91/0 | 4.5009 | 384 | 1447.0294 | 30 | 4000 | 9999 | 1 | 0
BUTTE | 0.2156 | 0.2523 | 158.6 | 16.307 | 6 | 19/0 | 3.2588 | 49 | 158.4513 | 12 | 436.9 | 9999 | 1 | 0
ALLIANCE | 0.2728 | 0.3194 | 125.15 | 14.3 | 6 | 7/0 | 4.7701 | 38 | 125.0965 | 6 | 345 | 9999 | 1 | 0
AKRON | 2.1996 | 2.5725 | 15.71 | 5.029 | 6 | 7/0 | 1.6789 | 5 | 15.4838 | 6 | 42.7 | 9999 | 1 | 0
DARIEN | 0.1212 | 0.1417 | 283.25 | 21.793 | 6 | 19/0 | 4.3586 | 84 | 283.4833 | 12 | 781.6 | 9999 | 1 | 0
AMHERST | 0.3442 | 0.4026 | 99.31 | 12.751 | 6 | 7/0 | 4.2469 | 30 | 99.1611 | 6 | 273.4 | 9999 | 1 | 0
ANAHEIM | 0.4331 | 0.507 | 78.54 | 11.354 | 6 | 7/0 | 3.7846 | 24 | 78.774 | 6 | 217.1 | 9999 | 1 | 0
SAPPHIRE | 0.0981 | 0.0991 | 346 | 26.289 | 6 | 37/0 | 3.749 | 115 | 408.7089 | 18 | 1120 | 9999 | 1 | 0
GREELEY | 0.0739 | 0.0864 | 469.71 | 28.143 | 6 | 37/0 | 4.0208 | 136 | 469.8055 | 18 | 1295.3 | 9999 | 1 | 0
FLINT | 0.092 | 0.1075 | 375.46 | 25.146 | 6 | 37/0 | 3.5941 | 109 | 375.3541 | 18 | 1034.9 | 9999 | 1 | 0
BLUEBIRD3 | 0.0289 | 9999 | 1185.17 | 44.755 | 7 | 42/19 | 4.9733 | 245 | 1185.1589 | 24 | 3265 | 9999 | 1 | 0
BLUEJAY1 | 0.0518 | 9999 | 606.52 | 31.979 | 7 | 30/7 | 4.5695 | 117 | 606.4504 | 18 | 1672.7 | 9999 | 1 | 0
BLUEJAY3 | 0.0541 | 9999 | 606.52 | 31.979 | 7 | 18/19 | 4.5695 | 144 | 606.4504 | 18 | 1672.7 | 9999 | 1 | 0
BLUEBIRD2 | 0.0286 | 9999 | 1185.17 | 44.755 | 7 | 48/13 | 4.9733 | 230 | 1185.1589 | 24 | 3265 | 9999 | 1 | 0
BLUEBIRD1 | 0.0282 | 9999 | 1185.17 | 44.755 | 7 | 54/7 | 4.9733 | 205 | 1185.1589 | 24 | 3265 | 9999 | 1 | 0
BUNTING1 | 0.049 | 9999 | 648.58 | 33.071 | 7 | 30/7 | 4.7244 | 125 | 648.3858 | 18 | 1787.3 | 9999 | 1 | 0
BUNTING3 | 0.0511 | 9999 | 648.58 | 33.071 | 7 | 18/19 | 4.7244 | 153 | 648.3858 | 18 | 1787.3 | 9999 | 1 | 0
BITTERN1 | 0.0459 | 9999 | 690.13 | 34.163 | 7 | 54/7 | 3.7871 | 122 | 690.3212 | 24 | 1901.9 | 9999 | 1 | 0
BLUEJAY2 | 0.0529 | 9999 | 606.52 | 31.979 | 7 | 24/13 | 4.5695 | 130 | 606.4504 | 18 | 1672.7 | 9999 | 1 | 0
BITTERN2 | 0.047 | 9999 | 690.13 | 34.163 | 7 | 42/19 | 3.7948 | 146 | 690.3212 | 24 | 1901.9 | 9999 | 1 | 0
BUNTING2 | 0.05 | 9999 | 648.58 | 33.071 | 7 | 24/13 | 4.7244 | 139 | 648.3858 | 18 | 1787.3 | 9999 | 1 | 0
DRAKE2 | 0.0675 | 9999 | 469.71 | 28.143 | 7 | 24/13 | 4.0208 | 101 | 469.8055 | 18 | 1295.3 | 9999 | 1 | 0
CURLEW1 | 0.0525 | 9999 | 593.85 | 31.648 | 7 | 33/4 | 4.5212 | 103 | 593.5472 | 18 | 1637 | 9999 | 1 | 0
GROSBEAK4 | 0.0856 | 9999 | 374.96 | 25.146 | 7 | 18/19 | 3.5916 | 89 | 374.967 | 18 | 1034.3 | 9999 | 1 | 0
GROSBEAK3 | 0.0838 | 9999 | 374.96 | 25.146 | 7 | 24/13 | 3.5916 | 81 | 374.967 | 18 | 1034.3 | 9999 | 1 | 0
GROSBEAK2 | 0.0819 | 9999 | 374.96 | 25.146 | 7 | 30/7 | 3.5916 | 73 | 374.967 | 18 | 1034.3 | 9999 | 1 | 0
GROSBEAK1 | 0.0806 | 9999 | 374.96 | 25.146 | 7 | 33/4 | 3.5916 | 66 | 374.967 | 18 | 1034.3 | 9999 | 1 | 0
DRAKE6 | 0.0741 | 9999 | 414.99 | 26.467 | 7 | 30/7 | 3.7795 | 81 | 469.8055 | 18 | 1144.4 | 9999 | 1 | 0
CARDINAL1 | 0.0572 | 9999 | 547.74 | 30.378 | 7 | 30/7 | 4.3409 | 105 | 547.5473 | 18 | 1510.5 | 9999 | 1 | 0
DRAKE3 | 0.0694 | 9999 | 469.71 | 28.143 | 7 | 18/19 | 4.0208 | 104 | 469.8055 | 18 | 1295.3 | 9999 | 1 | 0
KIWI3 | 0.0298 | 9999 | 1148.69 | 44.069 | 7 | 42/19 | 4.8971 | 237 | 1149.03 | 24 | 3165.3 | 9999 | 1 | 0
DRAKE1 | 0.0657 | 9999 | 469.71 | 28.143 | 7 | 30/7 | 4.0208 | 90 | 469.8055 | 18 | 1295.3 | 9999 | 1 | 0
PELICAN2 | 0.122 | 9999 | 255.38 | 20.676 | 7 | 12/7 | 4.1351 | 55 | 254.8382 | 12 | 703.9 | 9999 | 1 | 0
DOVE2 | 0.0948 | 9999 | 330.88 | 23.546 | 7 | 12/7 | 4.7092 | 72 | 330.9026 | 12 | 912.2 | 9999 | 1 | 0
CURLEW4 | 0.0554 | 9999 | 593.85 | 31.648 | 7 | 18/19 | 4.5212 | 141 | 593.5472 | 18 | 1637 | 9999 | 1 | 0
CURLEW3 | 0.0542 | 9999 | 593.85 | 31.648 | 7 | 24/13 | 4.5212 | 127 | 593.5472 | 18 | 1637 | 9999 | 1 | 0
CURLEW2 | 0.0531 | 9999 | 593.85 | 31.648 | 7 | 30/7 | 4.5212 | 114 | 593.5472 | 18 | 1637 | 9999 | 1 | 0
DRAKE5 | 0.0741 | 9999 | 425.63 | 26.797 | 7 | 24/13 | 3.8278 | 91 | 469.8055 | 18 | 1174.2 | 9999 | 1 | 0
RAIL3 | 0.0625 | 9999 | 518.86 | 29.591 | 7 | 18/19 | 4.2266 | 123 | 519.0957 | 18 | 1431.2 | 9999 | 1 | 0
PELICAN1 | 0.1196 | 9999 | 255.38 | 20.676 | 7 | 15/4 | 4.1351 | 50 | 254.8382 | 12 | 702.6 | 9999 | 1 | 0
ORTOLAN3 | 0.0582 | 9999 | 561.93 | 30.785 | 7 | 18/19 | 4.3967 | 133 | 561.9344 | 18 | 1549.2 | 9999 | 1 | 0
ORTOLAN2 | 0.057 | 9999 | 561.93 | 30.785 | 7 | 24/13 | 4.3967 | 120 | 561.9344 | 18 | 1549.2 | 9999 | 1 | 0
ORTOLAN1 | 0.0557 | 9999 | 561.93 | 30.785 | 7 | 30/7 | 4.3967 | 108 | 561.9344 | 18 | 1549.2 | 9999 | 1 | 0
MERLIN2 | 0.1727 | 9999 | 179.88 | 17.348 | 7 | 12/7 | 3.4722 | 40 | 179.9351 | 12 | 495.6 | 9999 | 1 | 0
MERLIN1 | 0.1685 | 9999 | 179.88 | 17.348 | 7 | 15/4 | 3.4722 | 36 | 179.9351 | 12 | 496 | 9999 | 1 | 0
KIWI1 | 0.0291 | 9999 | 1148.69 | 44.069 | 7 | 54/7 | 4.8971 | 199 | 1149.03 | 24 | 3165.3 | 9999 | 1 | 0
RAIL2 | 0.0613 | 9999 | 518.86 | 29.591 | 7 | 24/13 | 4.2266 | 111 | 519.0957 | 18 | 1431.2 | 9999 | 1 | 0
KIWI2 | 0.0295 | 9999 | 1148.69 | 44.069 | 7 | 48/13 | 4.8971 | 222 | 1149.03 | 24 | 3165.3 | 9999 | 1 | 0
RAIL4 | 0.062 | 9999 | 512.78 | 29.413 | 7 | 24/13 | 4.2012 | 110 | 519.0957 | 18 | 1413.8 | 9999 | 1 | 0
RAIL5 | 0.0628 | 9999 | 498.09 | 28.981 | 7 | 30/7 | 4.1402 | 96 | 519.0957 | 18 | 1373.6 | 9999 | 1 | 0
LAPWING3 | 0.0387 | 9999 | 862.91 | 38.202 | 7 | 42/19 | 4.2443 | 180 | 863.2241 | 24 | 2379.6 | 9999 | 1 | 0
LAPWING2 | 0.0382 | 9999 | 862.91 | 38.202 | 7 | 48/13 | 4.2443 | 169 | 863.2241 | 24 | 2379.6 | 9999 | 1 | 0
LAPWING1 | 0.0378 | 9999 | 862.91 | 38.202 | 7 | 54/7 | 4.2443 | 157 | 863.2241 | 24 | 2379.6 | 9999 | 1 | 0
DOVE1 | 0.0925 | 9999 | 330.88 | 23.546 | 7 | 15/4 | 4.7092 | 64 | 330.9026 | 12 | 912.2 | 9999 | 1 | 0
RAIL1 | 0.06 | 9999 | 518.86 | 29.591 | 7 | 30/7 | 4.2266 | 100 | 519.0957 | 18 | 1431.2 | 9999 | 1 | 0
CHAMERA | 0.0545 | 9999 | 587.77 | 31.496 | 7 | 30/7 | 4.5009 | 116 | 587.9988 | 18 | 1624 | 9999 | 1 | 0
CARDINAL2 | 0.0584 | 9999 | 547.74 | 30.378 | 7 | 24/13 | 4.3409 | 117 | 547.5473 | 18 | 1510.5 | 9999 | 1 | 0
CARDINAL3 | 0.0598 | 9999 | 547.74 | 30.378 | 7 | 18/19 | 4.3409 | 130 | 547.5473 | 18 | 1510.5 | 9999 | 1 | 0
TERN3 | 0.0748 | 9999 | 432.72 | 27 | 7 | 18/19 | 3.8583 | 102 | 432.5798 | 18 | 1192.6 | 9999 | 1 | 0
TERN2 | 0.073 | 9999 | 432.72 | 27 | 7 | 24/13 | 3.8583 | 93 | 432.5798 | 18 | 1192.6 | 9999 | 1 | 0
TERN1 | 0.0711 | 9999 | 432.72 | 27 | 7 | 30/7 | 3.8583 | 83 | 432.5798 | 18 | 1192.6 | 9999 | 1 | 0
CHUKAR1 | 0.0338 | 9999 | 979.45 | 40.691 | 7 | 54/7 | 4.5212 | 177 | 979.3529 | 24 | 2699.5 | 9999 | 1 | 0
CHUKAR2 | 0.0342 | 9999 | 979.45 | 40.691 | 7 | 48/13 | 4.5212 | 191 | 979.3529 | 24 | 2699.5 | 9999 | 1 | 0
CHUKAR3 | 0.0346 | 9999 | 979.45 | 40.691 | 7 | 42/19 | 4.5212 | 205 | 979.3529 | 24 | 2699.5 | 9999 | 1 | 0
3#6AW | 2.181 | 2.5737 | 39.88 | 8.865 | 8 | 3/0 | 2.954 | 46 | 39.8709 | 3 | 265 | 9999 | 1 | 0
7#10AW | 2.4109 | 2.8446 | 36.84 | 7.772 | 8 | 7/0 | 2.5908 | 45 | 36.8386 | 6 | 245.1 | 9999 | 1 | 0
37#9AW | 0.366 | 0.4319 | 245.34 | 20.345 | 8 | 37/0 | 2.9058 | 297 | 245.4834 | 18 | 1648.9 | 9999 | 1 | 0
37#8AW | 0.2902 | 0.3424 | 309.59 | 22.835 | 8 | 37/0 | 3.2614 | 375 | 309.5478 | 18 | 2080.4 | 9999 | 1 | 0
37#7AW | 0.1448 | 0.1709 | 390.36 | 25.654 | 8 | 37/0 | 3.6652 | 448 | 390.3218 | 18 | 2622.1 | 9999 | 1 | 0
37#6AW | 0.1827 | 0.215 | 492.01 | 28.804 | 8 | 37/0 | 4.0996 | 535 | 492.1926 | 18 | 3306.7 | 9999 | 1 | 0
37#5AW | 0.1448 | 0.1709 | 620.3 | 32.334 | 8 | 37/0 | 4.6076 | 635 | 620.5794 | 18 | 4169.8 | 9999 | 1 | 0
7#5AW | 0.7705 | 0.9091 | 117.35 | 13.868 | 8 | 7/0 | 4.6228 | 120 | 117.4191 | 6 | 781.1 | 9999 | 1 | 0
7#6AW | 0.9544 | 1.1259 | 93.08 | 12.344 | 8 | 7/0 | 4.1148 | 101 | 93.0966 | 6 | 619.5 | 9999 | 1 | 0
7#7AW | 1.2036 | 1.4205 | 73.88 | 10.998 | 8 | 7/0 | 3.6576 | 85 | 73.8708 | 6 | 491.1 | 9999 | 1 | 0
3#9AW | 4.3744 | 5.1617 | 19.91 | 6.248 | 8 | 3/0 | 2.0904 | 25 | 19.8709 | 3 | 132.1 | 9999 | 1 | 0
3#7AW | 2.7465 | 3.2411 | 31.67 | 7.899 | 8 | 3/0 | 2.634 | 38 | 31.6128 | 3 | 210.1 | 9999 | 1 | 0
37#10AW | 0.4604 | 0.5431 | 194.67 | 18.11 | 8 | 37/0 | 2.5883 | 236 | 194.6448 | 18 | 1308.1 | 9999 | 1 | 0
3#5AW | 1.7274 | 2.0381 | 50.32 | 9.957 | 8 | 3/0 | 3.3198 | 54 | 50.3225 | 3 | 334.1 | 9999 | 1 | 0
3#10AW | 5.5116 | 6.5039 | 15.81 | 5.588 | 8 | 3/0 | 1.8618 | 20 | 15.8064 | 3 | 104.8 | 9999 | 1 | 0
19#9AW | 0.7084 | 0.8357 | 126.02 | 14.529 | 8 | 19/0 | 2.9058 | 153 | 126.0643 | 12 | 842 | 9999 | 1 | 0
19#8AW | 0.5617 | 0.6624 | 158.95 | 16.307 | 8 | 19/0 | 3.2614 | 192 | 158.9674 | 12 | 1061.8 | 9999 | 1 | 0
19#7AW | 0.4455 | 0.5257 | 200.45 | 18.313 | 8 | 19/0 | 3.6627 | 230 | 200.4512 | 12 | 1338.6 | 9999 | 1 | 0
19#6AW | 0.3529 | 0.4169 | 252.64 | 20.574 | 8 | 19/0 | 4.1148 | 274 | 252.7092 | 12 | 1687.6 | 9999 | 1 | 0
19#5AW | 0.2802 | 0.3306 | 318.56 | 23.114 | 8 | 19/0 | 4.6228 | 326 | 318.709 | 12 | 2128.1 | 9999 | 1 | 0
19#10AW | 0.8929 | 1.0538 | 99.97 | 12.929 | 8 | 19/0 | 2.5857 | 121 | 99.9353 | 12 | 667.7 | 9999 | 1 | 0
7#8AW | 1.5161 | 1.7889 | 58.57 | 9.779 | 8 | 7/0 | 3.2512 | 71 | 58.5805 | 6 | 389.6 | 9999 | 1 | 0
7#9AW | 1.9138 | 2.2581 | 46.41 | 8.712 | 8 | 7/0 | 2.8956 | 56 | 46.4515 | 6 | 308.9 | 9999 | 1 | 0
3#8AW | 3.4672 | 4.0911 | 25.08 | 7.036 | 8 | 3/0 | 2.3444 | 32 | 25.0967 | 3 | 166.7 | 9999 | 1 | 0
5/8HS | 1.4105 | 1.6361 | 0 | 15.773 | 9 | 7/0 | 5.2578 | 132 | 151.9352 | 6 | 1209.9 | 9999 | 1 | 0
5/8EHS | 1.4416 | 1.6721 | 0 | 15.773 | 9 | 7/0 | 5.2578 | 189 | 151.9352 | 6 | 1209.9 | 9999 | 1 | 0
5/16EHS | 5.7166 | 6.6313 | 0 | 7.925 | 9 | 7/0 | 2.6416 | 50 | 38.387 | 6 | 305.1 | 9999 | 1 | 0
7/16EHS | 2.9453 | 3.4163 | 0 | 11.049 | 9 | 7/0 | 3.683 | 93 | 74.5805 | 6 | 593.8 | 9999 | 1 | 0
3/8EHS | 4.3061 | 4.9952 | 0 | 9.144 | 9 | 7/0 | 3.048 | 69 | 51.0967 | 6 | 406.3 | 9999 | 1 | 0
7/16HS | 2.8707 | 3.3299 | 0 | 11.049 | 9 | 7/0 | 3.683 | 64 | 74.5805 | 6 | 593.8 | 9999 | 1 | 0
1/2HS | 2.2183 | 2.5731 | 0 | 12.573 | 9 | 7/0 | 4.191 | 84 | 96.5805 | 6 | 769.4 | 9999 | 1 | 0
1/2EHS | 2.2742 | 2.6383 | 0 | 12.573 | 9 | 7/0 | 4.191 | 120 | 96.5805 | 6 | 769.4 | 9999 | 1 | 0
3/8HS | 4.1942 | 4.8653 | 0 | 9.144 | 9 | 7/0 | 3.048 | 48 | 51.0967 | 6 | 406.3 | 9999 | 1 | 0
CU2AWG-1 | 0.5435 | 0.6445 | 33.63 | 6.543 | 10 | 1/0 | 6.543 | 13 | 33.6128 | 1 | 299.1 | 9999 | 1 | 0
CU4/0AWG-7 | 0.1745 | 0.2067 | 107.22 | 13.251 | 10 | 7/0 | 4.4171 | 41 | 107.2901 | 6 | 972.2 | 9999 | 1 | 0
CU750-37 | 0.0514 | 0.0601 | 380.03 | 25.319 | 10 | 37/0 | 3.617 | 149 | 380.1928 | 18 | 3447.3 | 9999 | 1 | 0
CU2AWG-3 | 0.549 | 0.651 | 33.63 | 8.138 | 10 | 3/0 | 3.777 | 13 | 33.6128 | 3 | 301.9 | 9999 | 1 | 0
CU2AWG-7 | 0.5543 | 0.6573 | 33.63 | 7.422 | 10 | 7/0 | 2.474 | 14 | 33.6774 | 6 | 304.9 | 9999 | 1 | 0
CU3/0AWG-1 | 0.2136 | 0.2533 | 85.02 | 10.404 | 10 | 1/0 | 10.4038 | 30 | 85.0321 | 1 | 756 | 9999 | 1 | 0
CU3/0AWG-12 | 0.2197 | 0.2604 | 85.02 | 12.484 | 10 | 12/0 | 3.0048 | 34 | 85.0966 | 6 | 771.6 | 9999 | 1 | 0
CU3/0AWG-19 | 0.2197 | 0.2604 | 85.02 | 11.481 | 10 | 19/0 | 2.2962 | 32 | 78.645 | 12 | 713.4 | 9999 | 1 | 0
CU3/0AWG-7 | 0.2197 | 0.2604 | 85.02 | 11.796 | 10 | 7/0 | 3.9319 | 33 | 84.9676 | 6 | 770.7 | 9999 | 1 | 0
CU500-37 | 0.0751 | 0.0885 | 253.35 | 20.66 | 10 | 37/0 | 2.9515 | 100 | 253.1608 | 18 | 2295.5 | 9999 | 1 | 0
CU5AWG-1 | 1.0894 | 1.2919 | 16.77 | 4.62 | 10 | 1/0 | 4.6203 | 7 | 16.7742 | 1 | 148.8 | 9999 | 1 | 0
CU600-37 | 0.0627 | 0.0738 | 304.02 | 22.634 | 10 | 37/0 | 3.2334 | 120 | 303.8058 | 18 | 2755 | 9999 | 1 | 0
CU300-19 | 0.1235 | 0.1462 | 152.01 | 15.964 | 10 | 19/0 | 3.1928 | 60 | 152.1287 | 12 | 1379.4 | 9999 | 1 | 0
CU300-12 | 0.1235 | 0.1462 | 152.01 | 16.685 | 10 | 12/0 | 4.0157 | 59 | 151.9997 | 6 | 1378.2 | 9999 | 1 | 0
CU900-61 | 0.0436 | 0.0508 | 456.03 | 27.775 | 10 | 61/0 | 3.0861 | 180 | 456.2572 | 24 | 4137.5 | 9999 | 1 | 0
CU350-19 | 0.1062 | 0.1256 | 177.35 | 17.234 | 10 | 19/0 | 3.4468 | 69 | 177.29 | 12 | 1607.7 | 9999 | 1 | 0
CU600-61 | 0.0632 | 0.0743 | 304.02 | 22.677 | 10 | 61/0 | 2.5197 | 122 | 304.1929 | 24 | 2758.2 | 9999 | 1 | 0
CU6AWG-1 | 1.3741 | 1.6296 | 13.3 | 4.115 | 10 | 1/0 | 4.1148 | 6 | 13.2903 | 1 | 117.6 | 9999 | 1 | 0
CU700-37 | 0.0547 | 0.0642 | 354.69 | 24.448 | 10 | 37/0 | 3.4925 | 139 | 354.4509 | 18 | 3214.1 | 9999 | 1 | 0
CU900-37 | 0.0436 | 0.0508 | 456.03 | 27.737 | 10 | 37/0 | 3.9624 | 176 | 456.2572 | 18 | 4137.2 | 9999 | 1 | 0
CU8AWG-1 | 2.1836 | 2.5896 | 8.37 | 3.264 | 10 | 1/0 | 3.2639 | 4 | 8.3871 | 1 | 74.4 | 9999 | 1 | 0
CU800-61 | 0.0485 | 0.0566 | 405.36 | 26.175 | 10 | 61/0 | 2.9083 | 161 | 405.225 | 24 | 3674.6 | 9999 | 1 | 0
CU800-37 | 0.0485 | 0.0566 | 405.36 | 26.137 | 10 | 37/0 | 3.7338 | 156 | 405.1605 | 18 | 3673.7 | 9999 | 1 | 0
CU7AWG-1 | 1.7316 | 2.0536 | 10.55 | 3.665 | 10 | 1/0 | 3.6652 | 5 | 10.5806 | 1 | 93.8 | 9999 | 1 | 0
CU750-61 | 0.0514 | 0.0601 | 380.03 | 25.352 | 10 | 61/0 | 2.8169 | 152 | 380.1283 | 24 | 3447.2 | 9999 | 1 | 0
CU700-61 | 0.0547 | 0.0642 | 354.69 | 24.483 | 10 | 61/0 | 2.7203 | 141 | 354.5154 | 24 | 3214.9 | 9999 | 1 | 0
CU400-19 | 0.0932 | 0.1101 | 202.68 | 18.428 | 10 | 19/0 | 3.6855 | 79 | 202.7093 | 12 | 1838 | 9999 | 1 | 0
CU400-37 | 0.0932 | 0.1101 | 202.68 | 18.491 | 10 | 37/0 | 2.6416 | 81 | 202.7738 | 18 | 1838.8 | 9999 | 1 | 0
CU300-37 | 0.1235 | 0.1462 | 152.01 | 16.002 | 10 | 37/0 | 2.286 | 62 | 151.8707 | 18 | 1377 | 9999 | 1 | 0
CU1/0AWG-7 | 0.3421 | 0.4137 | 53.46 | 9.357 | 10 | 7/0 | 3.1191 | 21 | 53.4838 | 6 | 485 | 9999 | 1 | 0
CU250-37 | 0.1479 | 0.1752 | 126.68 | 14.615 | 10 | 37/0 | 2.0879 | 52 | 126.7094 | 18 | 1148.7 | 9999 | 1 | 0
CU250-19 | 0.1479 | 0.1752 | 126.68 | 14.567 | 10 | 19/0 | 2.9134 | 51 | 126.6449 | 12 | 1148.6 | 9999 | 1 | 0
CU250-12 | 0.1479 | 0.1752 | 126.68 | 15.23 | 10 | 12/0 | 3.6652 | 49 | 126.5804 | 6 | 1148.1 | 9999 | 1 | 0
CU2/0AWG-7 | 0.2768 | 0.328 | 67.44 | 10.508 | 10 | 7/0 | 3.5027 | 26 | 67.4192 | 6 | 611.6 | 9999 | 1 | 0
CU2/0AWG19 | 0.2768 | 0.328 | 67.44 | 10.63 | 10 | 19/0 | 2.126 | 27 | 67.4192 | 12 | 611.6 | 9999 | 1 | 0
CU450-19 | 0.0831 | 0.0981 | 228.02 | 19.545 | 10 | 19/0 | 3.9091 | 88 | 227.9995 | 12 | 2067.8 | 9999 | 1 | 0
CU450-37 | 0.0831 | 0.0981 | 228.02 | 19.611 | 10 | 37/0 | 2.8016 | 91 | 228.0641 | 18 | 2068.2 | 9999 | 1 | 0
CU2/0AWG-1 | 0.269 | 0.3191 | 67.44 | 9.266 | 10 | 1/0 | 9.2659 | 25 | 67.4192 | 1 | 599.7 | 9999 | 1 | 0
CU1AWG-7 | 0.4397 | 0.5214 | 42.41 | 8.329 | 10 | 7/0 | 2.7762 | 17 | 42.387 | 6 | 384.5 | 9999 | 1 | 0
CU1AWG-3 | 0.4354 | 0.5163 | 42.41 | 9.141 | 10 | 3/0 | 4.2418 | 16 | 42.387 | 3 | 380.8 | 9999 | 1 | 0
CU1AWG-1 | 0.4311 | 0.5111 | 42.41 | 7.348 | 10 | 1/0 | 7.3482 | 16 | 42.387 | 1 | 376.5 | 9999 | 1 | 0
CU4AWG-1 | 0.8639 | 1.0245 | 21.15 | 5.189 | 10 | 1/0 | 5.1892 | 9 | 21.1612 | 1 | 187.5 | 9999 | 1 | 0
CU1000-61 | 0.0398 | 0.0462 | 506.7 | 29.261 | 10 | 61/0 | 3.2512 | 200 | 506.3861 | 24 | 4592.2 | 9999 | 1 | 0
CU1000-37 | 0.0398 | 0.0462 | 506.7 | 29.23 | 10 | 37/0 | 4.1758 | 195 | 506.7087 | 18 | 4594.8 | 9999 | 1 | 0
CU4/0AWG-19 | 0.1745 | 0.2067 | 107.22 | 13.399 | 10 | 19/0 | 2.6797 | 43 | 107.1611 | 12 | 971.6 | 9999 | 1 | 0
CU350-37 | 0.1062 | 0.1256 | 177.35 | 17.3 | 10 | 37/0 | 2.4714 | 72 | 177.4835 | 18 | 1609.4 | 9999 | 1 | 0
CU350-12 | 0.1062 | 0.1256 | 177.35 | 18.026 | 10 | 12/0 | 4.3383 | 67 | 177.3545 | 6 | 1608.6 | 9999 | 1 | 0
CU3AWG-1 | 0.6854 | 0.8128 | 26.67 | 5.827 | 10 | 1/0 | 5.8268 | 11 | 26.6451 | 1 | 236.6 | 9999 | 1 | 0
CU3AWG-3 | 0.6922 | 0.8209 | 26.67 | 7.252 | 10 | 3/0 | 3.3655 | 10 | 26.7096 | 3 | 239.4 | 9999 | 1 | 0
CU3AWG-7 | 0.6989 | 0.8288 | 26.67 | 6.607 | 10 | 7/0 | 2.2022 | 11 | 26.6451 | 6 | 241.8 | 9999 | 1 | 0
CU4AWG-3 | 0.8725 | 1.0348 | 21.15 | 6.459 | 10 | 3/0 | 2.9972 | 8 | 21.1612 | 3 | 189.9 | 9999 | 1 | 0
CU4/0AWG-12 | 0.1745 | 0.2067 | 107.22 | 14.016 | 10 | 12/0 | 3.3731 | 42 | 107.2256 | 6 | 972.4 | 9999 | 1 | 0
CU500-19 | 0.0751 | 0.0885 | 253.35 | 20.599 | 10 | 19/0 | 4.1199 | 97 | 253.2898 | 12 | 2296.8 | 9999 | 1 | 0
CU4AWG-7 | 0.8812 | 1.045 | 21.15 | 5.883 | 10 | 7/0 | 1.9609 | 9 | 21.1612 | 6 | 191.8 | 9999 | 1 | 0
CU1/0AWG-1 | 0.3392 | 0.4025 | 53.46 | 8.252 | 10 | 1/0 | 8.2525 | 20 | 53.4838 | 1 | 476.2 | 9999 | 1 | 0
CU1/0AWG-19 | 0.3489 | 0.4137 | 53.46 | 9.462 | 10 | 19/0 | 1.8923 | 22 | 53.4192 | 12 | 484.5 | 9999 | 1 | 0
CU4/0AWG-1 | 0.1696 | 0.2011 | 107.22 | 11.684 | 10 | 1/0 | 11.684 | 36 | 107.2256 | 1 | 953.9 | 9999 | 1 | 0
1113-T13/3M/ACCR | 0.0509 | 0.061 | 563.96 | 32.766 | 11 | 54/19 | 3.6576 | 170 | 635.4826 | 24 | 1812.6 | 0.00254 | 1 | 0
1033-T13/3M/ACCR | 0.0548 | 0.0657 | 523.42 | 31.496 | 11 | 54/19 | 3.5052 | 158 | 589.6762 | 24 | 1681.6 | 0.00254 | 1 | 0
1272-T13/3M/ACCR | 0.0446 | 0.0533 | 644.52 | 35.052 | 11 | 54/19 | 3.8862 | 194 | 726.4502 | 24 | 2071.5 | 0.00254 | 1 | 0
1351-T13/3M/ACCR | 0.0419 | 0.0502 | 684.55 | 36.068 | 11 | 54/19 | 4.0132 | 206 | 770.9662 | 24 | 2199.5 | 0.00254 | 1 | 0
636-T16/3M/ACCR | 0.0874 | 0.1048 | 322.26 | 25.146 | 11 | 26/19 | 3.9624 | 112 | 373.5476 | 16 | 1067 | 0.00254 | 1 | 0
954-T13/3M/ACCR | 0.0593 | 0.0711 | 483.39 | 30.48 | 11 | 54/19 | 3.3782 | 146 | 544.515 | 24 | 1553.6 | 0.00254 | 1 | 0
477-T16/3M/ACCR | 0.1165 | 0.1396 | 241.7 | 21.844 | 11 | 26/7 | 3.429 | 87 | 280.6446 | 16 | 802.1 | 0.00254 | 1 | 0
1590-T13/3M/ACCR | 0.0356 | 0.0427 | 805.65 | 39.116 | 11 | 54/19 | 4.3688 | 243 | 907.7401 | 24 | 2589.4 | 0.00254 | 1 | 0
556-T16/3M/ACCR | 0.0998 | 0.1196 | 281.73 | 23.622 | 11 | 26/7 | 3.7084 | 101 | 327.7413 | 16 | 937.5 | 0.00254 | 1 | 0
795-T16/3M/ACCR | 0.07 | 0.0838 | 402.83 | 28.143 | 11 | 26/19 | 4.4425 | 138 | 466.9668 | 16 | 1333.4 | 0.00254 | 1 | 0
397-T16/3M/ACCR | 0.1398 | 0.1675 | 201.16 | 19.812 | 11 | 26/7 | 3.1496 | 73 | 234.1931 | 16 | 668.2 | 0.00254 | 1 | 0
336-T16/3M/ACCR | 0.1652 | 0.1979 | 170.25 | 18.288 | 11 | 26/7 | 2.8956 | 62 | 198.0641 | 16 | 565.5 | 0.00254 | 1 | 0
BLUEBIRD/ACCC/TW | 0.0246 | 0.0283 | 1381.7709 | 44.7548 | 12 | 64/1 | 5.2451 | 266.0143 | 1469.4809 | 23 | 4012.0901 | 10.541 | 1 | 0
CHUCKAR/ACCC/TW | 0.0285 | 0.0332 | 1136.0214 | 40.6908 | 12 | 56/1 | 5.0825 | 234.4307 | 1215.2234 | 20 | 3311.1649 | 10.033 | 1 | 0
LAPWING/ACCC/TW | 0.0317 | 0.0372 | 996.1722 | 38.2016 | 12 | 56/1 | 4.7752 | 217.9716 | 1071.4817 | 20 | 2916.8014 | 9.779 | 1 | 0
LINNET/ACCC/TW | 0.1312 | 0.1577 | 218.3877 | 18.288 | 12 | 16/1 | 4.1681 | 72.5089 | 246.3866 | 10 | 653.304 | 5.969 | 1 | 0
GROSBEAK/ACCC/TW | 0.07 | 0.0839 | 413.4672 | 25.146 | 12 | 19/1 | 5.2629 | 135.2314 | 465.4829 | 12 | 1238.1524 | 8.128 | 1 | 0
DOVE/ACCC/TW | 0.0799 | 0.0958 | 361.2771 | 23.5458 | 12 | 18/1 | 5.0546 | 122.331 | 408.2572 | 11 | 1081.8952 | 7.747 | 1 | 0
HAWK/ACCC/TW | 0.0929 | 0.1116 | 309.5937 | 21.7932 | 12 | 16/1 | 4.9886 | 103.2029 | 349.3541 | 10 | 927.1262 | 7.112 | 1 | 0
CARDINAL/ACCC/TW | 0.0479 | 0.0571 | 619.1874 | 30.3784 | 12 | 36/1 | 4.6812 | 165.0356 | 679.7406 | 16 | 1827.4654 | 8.763 | 1 | 0
BITTERN/ACCC/TW | 0.0382 | 0.0451 | 796.5324 | 34.163 | 12 | 39/1 | 5.1003 | 174.8221 | 856.966 | 18 | 2312.6069 | 8.763 | 1 | 0
DRAKE/ACCC/TW | 0.0564 | 0.0675 | 516.834 | 28.1432 | 12 | 22/1 | 5.4712 | 182.8292 | 588.1279 | 14 | 1556.6195 | 9.525 | 1 | 0
1_5BusAlumTube | 0.0642 | 0.0752 | 506.19 | 48.26 | 13 | 99/0 | 2.54 | 445 | 515.8054 | 99 | 1398.9 | 9999 | 1 | 0
1_0BusAlumTube | 0.104 | 0.1218 | 506.19 | 33.401 | 13 | 99/0 | 2.54 | 445 | 318.6445 | 99 | 864.6 | 9999 | 1 | 0
3_5BusAlumTube | 0.0192 | 0.0225 | 506.19 | 101.6 | 13 | 99/0 | 2.54 | 445 | 1729.0288 | 99 | 4689.2 | 9999 | 1 | 0
6_0BusAlumTube | 0.0093 | 0.0109 | 506.19 | 168.275 | 13 | 99/0 | 2.54 | 445 | 3600.638 | 99 | 9768.3 | 9999 | 1 | 0
2_5BusAlumTube | 0.0302 | 0.0354 | 506.19 | 73.025 | 13 | 99/0 | 2.54 | 445 | 1099.3526 | 99 | 2982.3 | 9999 | 1 | 0
5_0BusAlumTube | 0.012 | 0.014 | 506.19 | 141.3 | 13 | 99/0 | 2.54 | 445 | 2774.188 | 99 | 7525.6 | 9999 | 1 | 0
4_0BusAlumTube | 0.0162 | 0.019 | 506.19 | 114.3 | 13 | 99/0 | 2.54 | 445 | 2047.7378 | 99 | 5555.3 | 9999 | 1 | 0
3_0BusAlumTube | 0.0231 | 0.027 | 506.19 | 88.9 | 13 | 99/0 | 2.54 | 445 | 1437.4165 | 99 | 3900.5 | 9999 | 1 | 0
2_0BusAlumTube | 0.0478 | 0.056 | 506.19 | 60.325 | 13 | 99/0 | 2.54 | 445 | 693.547 | 99 | 1881 | 9999 | 1 | 0
0_75BusCuTube | 0.0757 | 0.09 | 506.19 | 26.67 | 14 | 99/0 | 2.54 | 445 | 216.2576 | 99 | 1934.6 | 9999 | 1 | 0
3_5BusCuTube | 0.0116 | 0.0137 | 506.19 | 101.6 | 14 | 99/0 | 2.54 | 445 | 1899.9962 | 99 | 16935.3 | 9999 | 1 | 0
4_0BusCuTube | 0.0094 | 0.0111 | 506.19 | 114.3 | 14 | 99/0 | 2.54 | 445 | 2153.5441 | 99 | 19197.3 | 9999 | 1 | 0
1_0BusCuTube | 0.0538 | 0.0639 | 506.19 | 33.401 | 14 | 99/0 | 2.54 | 445 | 304.7091 | 99 | 2723.3 | 9999 | 1 | 0
1_25BusCuTube | 0.0426 | 0.0506 | 506.19 | 42.164 | 14 | 99/0 | 2.54 | 445 | 447.9991 | 99 | 3988.3 | 9999 | 1 | 0
1_5BusCuTube | 0.0359 | 0.0427 | 506.19 | 48.26 | 14 | 99/0 | 2.54 | 445 | 532.0635 | 99 | 4747.2 | 9999 | 1 | 0
2_5BusCuTube | 0.0153 | 0.0182 | 506.19 | 73.025 | 14 | 99/0 | 2.54 | 445 | 1021.2883 | 99 | 9107.5 | 9999 | 1 | 0
2_0BusCuTube | 0.0263 | 0.0313 | 506.19 | 60.325 | 14 | 99/0 | 2.54 | 445 | 703.8696 | 99 | 6265.2 | 9999 | 1 | 0
3_0BusCuTube | 0.0128 | 0.0152 | 506.19 | 88.9 | 14 | 99/0 | 2.54 | 445 | 1456.1261 | 99 | 12976.8 | 9999 | 1 | 0

## RateKit US
RateKit US Database
Conductor_US | Rac@25C | Rac@75C | Alum_kcmil | OD | CDR_Type | Strand_Ratio | Diam-Outer | UTS | Area | Std-OL | Weight | Diam-Inner | b | m
ROOK/TW | 0.1432 | 0.1717 | 636 | 0.89 | 1 | 19/7 | 0.183 | 22900 | 0.5643 | 11 | 816 | 0.1085 | 1 | 0
CHUKAR/AW | 0.0553 | 0.0649 | 1781 | 1.602 | 1 | 84/19 | 0.1456 | 49700 | 1.513 | 30 | 2015 | 0.0874 | 1 | 0
REDWING/AW | 0.1228 | 0.1466 | 715.5 | 1.081 | 1 | 30/19 | 0.1544 | 33400 | 0.6896 | 18 | 1044 | 0.0926 | 1 | 0
CATAWBA/TW | 0.0747 | 0.0888 | 1272 | 1.203 | 1 | 30/7 | 0.2059 | 31400 | 1.0505 | 14 | 1372 | 0.0967 | 1 | 0
RICE | 0.0587 | 0.0666 | 1847.21 | 1.685 | 1 | 54/19 | 0.187 | 62272.0719 | 1.6709 | 24 | 2419.092 | 0.1122 | 1 | 0
RINGDOVE/SD | 0.0726 | 9999 | 1351.5 | 1.334 | 1 | 42/7 | 0.168 | 33400 | 1.116 | 21 | 1458 | 0.0997 | 1 | 0
RIO GRANDE/TW | 0.0618 | 0.0734 | 1533.3 | 1.382 | 1 | 39/19 | 0.1983 | 53200 | 1.3571 | 17 | 1968 | 0.1012 | 1 | 0
ROBIN | 1.087 | 1.427 | 83.69 | 0.354 | 1 | 6/1 | 0.1181 | 3550 | 0.0767 | 6 | 115.1 | 0.1181 | 1 | 0
ROBIN/AW | 1.047 | 1.252 | 83.7 | 0.354 | 1 | 6/1 | 0.1181 | 3550 | 0.0767 | 6 | 109.5 | 0.1181 | 1 | 0
ROBIN/T2 | 0.5858 | 0.682 | 167.4 | 0.581 | 1 | 6/1 | 0.1181 | 7100 | 0.1534 | 6 | 230.2 | 0.1181 | 1 | 0
ROOK | 0.146 | 0.174 | 636 | 0.977 | 1 | 24/7 | 0.1628 | 22600 | 0.5643 | 15 | 819.2 | 0.1085 | 1 | 0
ROOK/AW | 0.1422 | 0.1697 | 636 | 0.977 | 1 | 24/7 | 0.1628 | 22000 | 0.5643 | 15 | 785.6 | 0.0185 | 1 | 0
REDSTART | 0.104 | 9999 | 900 | 1.162 | 1 | 24/7 | 0.1936 | 31600 | 0.7981 | 15 | 1159 | 0.1291 | 1 | 0
ROOK/T2 | 0.074 | 9999 | 1272 | 1.599 | 1 | 24/7 | 0.1628 | 45400 | 1.1286 | 24 | 1638 | 0.1628 | 1 | 0
REDBIRD | 0.098 | 0.117 | 954 | 1.196 | 1 | 24/7 | 0.1994 | 33500 | 0.8466 | 15 | 1229 | 0.1329 | 1 | 0
CARROT | 0.5369 | 0.5987 | 207.22 | 0.563 | 1 | 6/7 | 0.187 | 7171 | 0.1866 | 6 | 271.5 | 0.063 | 1 | 0
CARDINAL/TW | 0.0962 | 0.1151 | 954 | 1.084 | 1 | 20/7 | 0.2184 | 33500 | 0.8464 | 12 | 1226 | 0.1329 | 1 | 0
CARDINAL/SD | 0.0983 | 9999 | 954 | 1.147 | 1 | 54/7 | 0.2122 | 33500 | 0.8464 | 13 | 1227 | 0.1329 | 1 | 0
RUDDY | 0.106 | 0.125 | 900 | 1.131 | 1 | 45/7 | 0.1414 | 24400 | 0.7555 | 21 | 1015 | 0.0943 | 1 | 0
RUDDY/AW | 0.1038 | 0.1235 | 900 | 1.131 | 1 | 45/7 | 0.1414 | 23970 | 0.7555 | 21 | 988.9 | 0.0943 | 1 | 0
CARDINAL/AW | 0.0959 | 0.1141 | 954 | 1.196 | 1 | 54/7 | 0.1383 | 32900 | 0.8462 | 24 | 1178 | 0.1329 | 1 | 0
SANTEE/TW | 0.0395 | 0.0459 | 2627.3 | 1.762 | 1 | 64/19 | 0.2026 | 74500 | 2.2268 | 22 | 3048 | 0.1062 | 1 | 0
SCHUYKILL/TW | 0.0584 | 0.069 | 1657.4 | 1.386 | 1 | 36/7 | 0.2146 | 44000 | 1.392 | 16 | 1868 | 0.128 | 1 | 0
SCISSORTAIL/TW | 0.0747 | 0.0889 | 1272 | 1.203 | 1 | 30/7 | 0.2059 | 31400 | 1.0505 | 14 | 1372 | 0.0967 | 1 | 0
SCISSORTL/SD | 0.0769 | 9999 | 1272 | 1.305 | 1 | 42/7 | 0.1631 | 31400 | 1.0503 | 21 | 1372 | 0.0967 | 1 | 0
CARDINAL | 0.0983 | 0.117 | 954 | 1.196 | 1 | 54/7 | 0.1329 | 33800 | 0.8462 | 24 | 1229 | 0.1329 | 1 | 0
ROOK/SD | 0.146 | 9999 | 636 | 0.955 | 1 | 24/7 | 0.1806 | 22900 | 0.5642 | 12 | 818 | 0.1085 | 1 | 0
LIME | 0.1966 | 0.1963 | 556.53 | 0.965 | 1 | 30/7 | 0.1378 | 27201.8798 | 0.5518 | 18 | 887.0004 | 0.1378 | 1 | 0
WAXWING/T2 | 0.1737 | 0.2073 | 533.6 | 0.997 | 1 | 18/1 | 0.1217 | 13800 | 0.442 | 12 | 578.8 | 0.1217 | 1 | 0
LAPWING/AW | 0.0613 | 0.0721 | 1590 | 1.504 | 1 | 45/7 | 0.188 | 41700 | 1.335 | 21 | 1748 | 0.1253 | 1 | 0
LAPWING/SD | 0.062 | 9999 | 1590 | 1.468 | 1 | 45/7 | 0.1835 | 42600 | 1.335 | 21 | 1791 | 0.1253 | 1 | 0
LAPWING/TW | 0.0606 | 0.0717 | 1590 | 1.358 | 1 | 36/7 | 0.2102 | 42200 | 1.3351 | 16 | 1791 | 0.1253 | 1 | 0
LARK | 0.229 | 0.274 | 397.5 | 0.806 | 1 | 30/7 | 0.1151 | 20300 | 0.3849 | 18 | 622.7 | 0.1151 | 1 | 0
LARK/AW | 0.2192 | 0.2621 | 397 | 0.806 | 1 | 30/7 | 0.1151 | 19600 | 0.3849 | 18 | 584.9 | 0.1151 | 1 | 0
CHUKAR | 0.0561 | 0.0658 | 1781 | 1.602 | 1 | 84/19 | 0.1456 | 51000 | 1.513 | 30 | 2075 | 0.0874 | 1 | 0
CHICKADEE/T2 | 0.1178 | 0.1401 | 795 | 1.216 | 1 | 18/1 | 0.1486 | 19900 | 0.659 | 12 | 863 | 0.1486 | 1 | 0
LEGHORN | 0.651 | 1 | 134.6 | 0.529 | 1 | 12/7 | 0.1059 | 13600 | 0.1674 | 12 | 335.9 | 0.1059 | 1 | 0
LEMON | 0.2706 | 0.2671 | 408.52 | 0.827 | 1 | 30/7 | 0.1181 | 20255.284 | 0.4053 | 18 | 653.8268 | 0.1181 | 1 | 0
CHICKADEE/AW | 0.231 | 0.2762 | 397 | 0.743 | 1 | 18/1 | 0.1486 | 9780 | 0.3295 | 12 | 422.6 | 0.1486 | 1 | 0
REDWING | 0.128 | 0.153 | 715.5 | 1.081 | 1 | 30/19 | 0.1544 | 34600 | 0.6896 | 18 | 1110 | 0.0926 | 1 | 0
CHEYENNE/TW | 0.081 | 0.0963 | 1168.1 | 1.155 | 1 | 30/7 | 0.1973 | 28900 | 0.9646 | 14 | 1260 | 0.0926 | 1 | 0
SMEW/SD | 0.0561 | 9999 | 1780 | 1.531 | 1 | 76/7 | 0.1914 | 43600 | 1.467 | 21 | 1921 | 0.1144 | 1 | 0
LINNET | 0.273 | 0.327 | 336.4 | 0.72 | 1 | 26/7 | 0.1137 | 14100 | 0.307 | 16 | 462.6 | 0.0884 | 1 | 0
LINNET/AW | 0.2644 | 0.3162 | 336.4 | 0.72 | 1 | 26/7 | 0.1137 | 13500 | 0.307 | 16 | 440.3 | 0.0884 | 1 | 0
LINNET/SD | 0.273 | 9999 | 336.4 | 0.716 | 1 | 26/7 | 0.1194 | 14300 | 0.3072 | 16 | 462.4 | 0.0884 | 1 | 0
LINNET/T2 | 0.1357 | 0.1615 | 672.8 | 1.18 | 1 | 26/7 | 0.1137 | 28200 | 0.6144 | 16 | 925 | 0.0884 | 1 | 0
CHERRY | 0.5369 | 0.5987 | 207.22 | 0.563 | 1 | 6/7 | 0.187 | 7464 | 0.1866 | 6 | 271.5 | 0.063 | 1 | 0
MACAW/SD | 0.1196 | 9999 | 795 | 0.999 | 1 | 42/7 | 0.216 | 19800 | 0.6565 | 11 | 856 | 0.0764 | 1 | 0
MACKENZIE/TW | 0.0698 | 0.0829 | 1359.7 | 1.259 | 1 | 36/7 | 0.1943 | 36900 | 1.1418 | 16 | 1530 | 0.1159 | 1 | 0
MALLARD | 0.116 | 0.138 | 795 | 1.14 | 1 | 30/19 | 0.1628 | 38400 | 0.7669 | 18 | 1235 | 0.0977 | 1 | 0
MALLARD/AW | 0.1107 | 0.132 | 795 | 1.14 | 1 | 30/19 | 0.1628 | 37100 | 0.7669 | 18 | 1161 | 0.0977 | 1 | 0
MANGO | 0.1468 | 0.153 | 736.12 | 1.063 | 1 | 54/7 | 0.1181 | 26527.453 | 0.6684 | 24 | 967.6368 | 0.1181 | 1 | 0
RAVEN/T2 | 0.4697 | 0.57 | 211.2 | 0.652 | 1 | 6/1 | 0.1327 | 8760 | 0.1936 | 6 | 290.4 | 0.1327 | 1 | 0
CHICKADEE | 0.234 | 0.279 | 397.5 | 0.743 | 1 | 18/1 | 0.1486 | 9940 | 0.3295 | 12 | 431.6 | 0.1486 | 1 | 0
TURKEY | 3.46 | 0.416 | 26.24 | 0.198 | 1 | 6/1 | 0.0661 | 1190 | 0.024 | 6 | 36.1 | 0.0661 | 1 | 0
TERN/SD | 0.119 | 9999 | 795 | 1.013 | 1 | 45/7 | 0.2144 | 21900 | 0.6676 | 11 | 893 | 0.0886 | 1 | 0
TERN/TW | 0.116 | 0.1388 | 795 | 0.96 | 1 | 17/7 | 0.2163 | 21800 | 0.6675 | 9 | 892 | 0.0886 | 1 | 0
CANARY | 0.104 | 0.124 | 900 | 1.162 | 1 | 54/7 | 0.1291 | 31900 | 0.7984 | 24 | 1159 | 0.1291 | 1 | 0
CAMEL | 0.1178 | 0.1238 | 918.28 | 1.188 | 1 | 54/7 | 0.1319 | 32552.3321 | 0.8348 | 24 | 1212.8387 | 0.1319 | 1 | 0
THAMES/TW | 0.0703 | 0.0837 | 1334.6 | 1.29 | 1 | 39/19 | 0.185 | 46300 | 1.1809 | 17 | 1713 | 0.0944 | 1 | 0
THRASHER | 0.0454 | 0.0528 | 2312 | 1.802 | 1 | 76/19 | 0.1744 | 56700 | 1.9144 | 28 | 2526 | 0.0814 | 1 | 0
THRASHER/AW | 0.0453 | 0.0524 | 2312 | 1.802 | 1 | 76/19 | 0.1744 | 55300 | 1.9144 | 28 | 2475 | 0.0814 | 1 | 0
TIGER | 0.4378 | 0.4104 | 253.2 | 0.651 | 1 | 30/7 | 0.0929 | 12719.6889 | 0.2513 | 18 | 406.6762 | 0.0929 | 1 | 0
CALUMET/TW | 0.1603 | 0.1923 | 565.3 | 0.858 | 1 | 18/7 | 0.1772 | 22900 | 0.5165 | 10 | 714.8 | 0.1147 | 1 | 0
CABBAGE | 0.8578 | 0.9447 | 128.67 | 0.445 | 1 | 6/1 | 0.1476 | 4833 | 0.1198 | 6 | 180.1 | 0.1476 | 1 | 0
TRUCKEE/TW | 0.0697 | 0.0826 | 1372.5 | 1.248 | 1 | 30/7 | 0.2139 | 33400 | 1.1334 | 14 | 1481 | 0.1004 | 1 | 0
SCOTER | 0.144 | 9999 | 636 | 1.019 | 1 | 30/7 | 0.1456 | 30800 | 0.6154 | 18 | 993 | 0.1456 | 1 | 0
TURBIT | 0.1185 | 9999 | 795 | 1.063 | 1 | 20/7 | 0.1994 | 21800 | 0.6678 | 13 | 896 | 0.0886 | 1 | 0
TEAL/AW | 0.1448 | 0.1729 | 605 | 0.994 | 1 | 30/19 | 0.142 | 28500 | 0.5834 | 18 | 883.2 | 0.0852 | 1 | 0
TURKEY/AW | 3.459 | 4.308 | 26.2 | 0.198 | 1 | 6/1 | 0.0661 | 1190 | 0.024 | 6 | 34.3 | 0.0661 | 1 | 0
TURNSTONE | 0.1052 | 9999 | 900 | 1.131 | 1 | 20/7 | 0.2121 | 24100 | 0.7555 | 13 | 1015 | 0.0943 | 1 | 0
BUNTING/TW | 0.0791 | 0.0941 | 1192.5 | 1.181 | 1 | 33/7 | 0.1901 | 32400 | 1.0013 | 15 | 1343 | 0.1085 | 1 | 0
BUNTING/SD | 0.0805 | 9999 | 1192.5 | 1.284 | 1 | 45/7 | 0.1604 | 32400 | 1.0013 | 21 | 1343 | 0.1085 | 1 | 0
BUNTING/AW | 0.0795 | 0.0942 | 1192.5 | 1.302 | 1 | 45/7 | 0.1628 | 31300 | 1.001 | 21 | 1311 | 0.1085 | 1 | 0
BUNTING | 0.0805 | 0.0954 | 1192.5 | 1.302 | 1 | 45/7 | 0.1628 | 32000 | 1.001 | 21 | 1344 | 0.1085 | 1 | 0
BROLGA | 0.123 | 0.1284 | 878.41 | 1.162 | 1 | 54/7 | 0.1291 | 31132 | 0.7985 | 24 | 1159.9 | 0.1291 | 1 | 0
WABASH/TW | 0.1191 | 0.1428 | 762.8 | 0.99 | 1 | 20/7 | 0.1953 | 30500 | 0.6966 | 12 | 1047 | 0.1331 | 1 | 0
BRANT/AW | 0.2262 | 0.2705 | 397.5 | 0.772 | 1 | 24/7 | 0.1287 | 14060 | 0.3527 | 15 | 491 | 0.0858 | 1 | 0
WAXWING | 0.347 | 0.416 | 266.8 | 0.609 | 1 | 18/1 | 0.1217 | 6880 | 0.221 | 12 | 289.5 | 0.1217 | 1 | 0
WAXWING/AW | 0.3435 | 0.4105 | 266.8 | 0.609 | 1 | 18/1 | 0.1217 | 6820 | 0.221 | 12 | 283.5 | 0.1217 | 1 | 0
BUTEO | 0.128 | 9999 | 715.5 | 1.081 | 1 | 30/7 | 0.1544 | 34400 | 0.6929 | 18 | 1119 | 0.1544 | 1 | 0
STILT | 0.1296 | 9999 | 715.5 | 1.036 | 1 | 24/7 | 0.1727 | 25500 | 0.6355 | 15 | 922 | 0.1151 | 1 | 0
CHUKAR/SD | 0.0561 | 9999 | 1780 | 1.565 | 1 | 84/19 | 0.1957 | 51100 | 1.513 | 21 | 2068 | 0.0874 | 1 | 0
SNOWBIRD | 0.0925 | 9999 | 1033.5 | 1.203 | 1 | 42/7 | 0.1569 | 25400 | 0.8539 | 21 | 1115.4 | 0.0872 | 1 | 0
SNOWBIRD/SD | 0.0934 | 9999 | 1033.5 | 1.185 | 1 | 42/7 | 0.1481 | 25900 | 0.8534 | 21 | 1115 | 0.0871 | 1 | 0
SNOWBIRD/TW | 0.0908 | 0.1083 | 1033.5 | 1.089 | 1 | 30/7 | 0.1856 | 25700 | 0.8534 | 14 | 1115 | 0.0871 | 1 | 0
SPARATE | 1.353 | 1.741 | 66.36 | 0.325 | 1 | 7/1 | 0.0974 | 3640 | 0.0654 | 7 | 106.7 | 0.1299 | 1 | 0
SPARATE/AW | 1.285 | 1.537 | 66.4 | 0.325 | 1 | 7/1 | 0.0974 | 3640 | 0.0654 | 7 | 99.9 | 0.1299 | 1 | 0
SPARROW/AW | 1.321 | 1.581 | 66.4 | 0.316 | 1 | 6/1 | 0.1052 | 2850 | 0.0608 | 6 | 86.8 | 0.1052 | 1 | 0
CANARY/AW | 0.1014 | 0.1207 | 900 | 1.162 | 1 | 54/7 | 0.1291 | 31000 | 0.7984 | 24 | 1111 | 0.1791 | 1 | 0
SQUAB | 0.153 | 0.182 | 605 | 0.966 | 1 | 26/7 | 0.1525 | 24300 | 0.5522 | 16 | 832.3 | 0.1186 | 1 | 0
SQUAB/AW | 0.1477 | 0.1764 | 605 | 0.966 | 1 | 26/7 | 0.1525 | 23600 | 0.5522 | 16 | 792.1 | 0.1186 | 1 | 0
ST CROIX/TW | 0.0655 | 0.0776 | 1467.8 | 1.292 | 1 | 33/7 | 0.2109 | 35800 | 1.2124 | 15 | 1585 | 0.1041 | 1 | 0
TERN/AW | 0.1169 | 0.1393 | 795 | 1.063 | 1 | 45/7 | 0.1329 | 21500 | 0.6674 | 21 | 873.4 | 0.0886 | 1 | 0
STARLING/AW | 0.1252 | 0.1494 | 716 | 1.051 | 1 | 26/7 | 0.1659 | 27500 | 0.6535 | 16 | 937.3 | 0.129 | 1 | 0
TERN | 0.119 | 0.141 | 795 | 1.063 | 1 | 45/7 | 0.1329 | 22100 | 0.6674 | 21 | 895.8 | 0.0886 | 1 | 0
SUWANNEE/TW | 0.0951 | 0.1138 | 959.6 | 1.108 | 1 | 22/7 | 0.2088 | 37000 | 0.8762 | 13 | 1318 | 0.1493 | 1 | 0
SWALLOW/T2 | 0.932 | 1.085 | 105.2 | 0.46 | 1 | 6/1 | 0.0937 | 4600 | 0.0964 | 6 | 145 | 0.0937 | 1 | 0
SWAN | 2.175 | 2.755 | 41.74 | 0.25 | 1 | 6/1 | 0.0834 | 1860 | 0.0382 | 6 | 57.4 | 0.0834 | 1 | 0
SWAN/AW | 2.102 | 2.516 | 41.7 | 0.25 | 1 | 6/1 | 0.0834 | 1860 | 0.0382 | 6 | 54.6 | 0.0834 | 1 | 0
SWAN/T2 | 1.0871 | 1.3608 | 83.5 | 0.409 | 1 | 6/1 | 0.0834 | 3720 | 0.0765 | 6 | 115.1 | 0.0834 | 1 | 0
SWANATE | 2.15 | 2.727 | 41.74 | 0.257 | 1 | 7/1 | 0.0772 | 2360 | 0.0411 | 7 | 67 | 0.1029 | 1 | 0
SWANATE/AW | 2.046 | 2.447 | 41.7 | 0.257 | 1 | 7/1 | 0.0772 | 2360 | 0.0411 | 7 | 62.7 | 0.1029 | 1 | 0
SWIFT | 0.148 | 0.176 | 636 | 0.93 | 1 | 36/1 | 0.1329 | 13800 | 0.5133 | 18 | 643.7 | 0.1329 | 1 | 0
SWIFT/TW | 0.1461 | 0.1748 | 636 | 0.85 | 1 | 27/1 | 0.1535 | 13500 | 0.5133 | 13 | 646 | 0.1329 | 1 | 0
TATLER/T2 | 0.0986 | 0.0117 | 954 | 1.347 | 1 | 20/7 | 0.1544 | 26400 | 0.8009 | 13 | 1074.4 | 0.0686 | 1 | 0
TEAL | 0.151 | 0.181 | 605 | 0.994 | 1 | 30/19 | 0.142 | 30000 | 0.5834 | 18 | 939.5 | 0.0852 | 1 | 0
SKIMMER | 0.116 | 9999 | 795 | 1.14 | 1 | 30/7 | 0.1628 | 38300 | 0.7704 | 18 | 1246 | 0.1628 | 1 | 0
STARLING | 0.129 | 0.154 | 715.5 | 1.051 | 1 | 26/7 | 0.1659 | 28400 | 0.6535 | 16 | 984.8 | 0.129 | 1 | 0
CROW/AW | 0.1267 | 0.1512 | 715.5 | 1.036 | 1 | 54/7 | 0.1151 | 25300 | 0.634 | 24 | 883.4 | 0.1151 | 1 | 0
LAPWING | 0.062 | 0.0729 | 1590 | 1.504 | 1 | 45/7 | 0.188 | 42200 | 1.335 | 21 | 1792 | 0.1253 | 1 | 0
FINCH | 0.0851 | 0.101 | 1113 | 1.293 | 1 | 54/19 | 0.1436 | 39100 | 0.9854 | 24 | 1431 | 0.0862 | 1 | 0
FINCH/AW | 0.0831 | 0.0987 | 1114 | 1.293 | 1 | 54/19 | 0.1436 | 37500 | 0.9854 | 24 | 1374 | 0.0862 | 1 | 0
FINCH/SD | 0.0851 | 9999 | 1113 | 1.233 | 1 | 54/19 | 0.2133 | 39100 | 0.985 | 15 | 1424 | 0.0862 | 1 | 0
FINCH/TW | 0.0837 | 0.0998 | 1113 | 1.185 | 1 | 38/19 | 0.1771 | 39100 | 0.9851 | 16 | 1429 | 0.0862 | 1 | 0
FLAMINGO | 0.139 | 0.166 | 666.6 | 1 | 1 | 24/7 | 0.1667 | 23700 | 0.5917 | 15 | 858.9 | 0.1111 | 1 | 0
FLAMINGO/AW | 0.1357 | 0.162 | 667 | 1 | 1 | 24/7 | 0.1667 | 23100 | 0.5917 | 15 | 823.7 | 0.1111 | 1 | 0
FLICKER | 0.194 | 0.232 | 477 | 0.846 | 1 | 24/7 | 0.141 | 17200 | 0.4233 | 15 | 614.6 | 0.094 | 1 | 0
FLICKER/AW | 0.1888 | 0.2256 | 477 | 0.846 | 1 | 24/7 | 0.141 | 16700 | 0.4233 | 15 | 589.4 | 0.094 | 1 | 0
FLICKER/SD | 0.194 | 9999 | 477 | 0.843 | 1 | 24/7 | 0.1502 | 17200 | 0.4233 | 13 | 613.5 | 0.094 | 1 | 0
FLICKER/T2 | 0.973 | 0.1155 | 954 | 1.305 | 1 | 24/7 | 0.141 | 34400 | 0.8464 | 15 | 1229 | 0.094 | 1 | 0
FALCON/SD | 0.0611 | 9999 | 1590 | 1.521 | 1 | 54/19 | 0.169 | 55100 | 1.407 | 24 | 2039 | 0.105 | 1 | 0
CUCKOO | 0.118 | 0.14 | 795 | 1.092 | 1 | 24/7 | 0.182 | 27900 | 0.7053 | 15 | 1024 | 0.1213 | 1 | 0
FALCON/AW | 0.0597 | 0.0704 | 1590 | 1.545 | 1 | 54/19 | 0.1716 | 53000 | 1.407 | 24 | 1962 | 0.105 | 1 | 0
FLYCATCHER/T2 | 0.0918 | 0.1088 | 1033.5 | 1.387 | 1 | 18/1 | 0.1694 | 25500 | 0.8564 | 12 | 1121.4 | 0.1694 | 1 | 0
FRASER/TW | 0.0982 | 0.1173 | 946.7 | 1.077 | 1 | 35/7 | 0.1645 | 29600 | 0.8168 | 16 | 1142 | 0.1154 | 1 | 0
FRIGATE/SD | 0.0718 | 9999 | 1351.5 | 1.389 | 1 | 22/7 | 0.1735 | 41700 | 1.155 | 21 | 1629 | 0.1377 | 1 | 0
GADWALL | 0.3073 | 9999 | 300 | 0.671 | 1 | 24/7 | 0.1118 | 14200 | 0.2666 | 15 | 386 | 0.0746 | 1 | 0
GANNET | 0.139 | 9999 | 666.6 | 1.014 | 1 | 26/7 | 0.1601 | 26400 | 0.6086 | 16 | 917.3 | 0.1245 | 1 | 0
GANNET/AW | 0.1252 | 0.1494 | 666.6 | 1.014 | 1 | 26/7 | 0.1601 | 26000 | 0.6086 | 16 | 873 | 0.1245 | 1 | 0
GARLIC | 0.2706 | 0.2671 | 408.52 | 0.827 | 1 | 30/7 | 0.1181 | 19603.3381 | 0.4053 | 18 | 653.8268 | 0.1181 | 1 | 0
CROW | 0.128 | 0.153 | 715.5 | 1.036 | 1 | 54/7 | 0.1151 | 26300 | 0.634 | 24 | 921 | 0.1151 | 1 | 0
GENESEE/TW | 0.0813 | 0.0968 | 1158 | 1.165 | 1 | 33/7 | 0.1873 | 31600 | 0.9733 | 15 | 1308 | 0.1078 | 1 | 0
CREEPER/T2 | 0.0916 | 0.1086 | 1033.5 | 1.403 | 1 | 20/7 | 0.1607 | 28300 | 0.8675 | 13 | 1163.8 | 0.0714 | 1 | 0
GOAT | 0.1779 | 0.1706 | 624.03 | 1.022 | 1 | 30/7 | 0.1461 | 30380.6779 | 0.6194 | 18 | 1001.9073 | 0.1461 | 1 | 0
FLICKER/TW | 0.1904 | 0.2284 | 477 | 0.776 | 1 | 18/7 | 0.1628 | 17200 | 0.4233 | 10 | 612.8 | 0.094 | 1 | 0
DRAKE | 0.117 | 0.139 | 795 | 1.108 | 1 | 26/7 | 0.1749 | 31500 | 0.7264 | 16 | 1094 | 0.136 | 1 | 0
CURLEW/TW | 0.0905 | 0.0976 | 1033.5 | 1.129 | 1 | 22/7 | 0.2167 | 36300 | 0.9169 | 13 | 1327 | 0.1383 | 1 | 0
DIPPER | 0.0717 | 0.0848 | 1351.5 | 1.386 | 1 | 45/7 | 0.1733 | 36200 | 1.134 | 21 | 1523 | 0.1155 | 1 | 0
DIPPER/AW | 0.0709 | 0.0837 | 1351 | 1.386 | 1 | 45/7 | 0.1733 | 35400 | 1.134 | 21 | 1485 | 0.1155 | 1 | 0
DIPPER/SD | 0.0717 | 9999 | 1351.5 | 1.361 | 1 | 45/7 | 0.1701 | 36700 | 1.134 | 21 | 1522 | 0.1155 | 1 | 0
DIPPER/TW | 0.0704 | 0.0836 | 1351.5 | 1.256 | 1 | 35/7 | 0.1965 | 36700 | 1.1348 | 16 | 1522 | 0.1155 | 1 | 0
DOG | 0.5345 | 0.6373 | 204.65 | 0.558 | 1 | 6/7 | 0.1858 | 7300 | 0.1842 | 6 | 265.3 | 0.0618 | 1 | 0
DOVE | 0.166 | 0.198 | 556.5 | 0.927 | 1 | 26/7 | 0.1463 | 22600 | 0.5083 | 16 | 766 | 0.1138 | 1 | 0
DOVE/AW | 0.1603 | 0.1915 | 556.5 | 0.927 | 1 | 26/7 | 0.1463 | 21900 | 0.5083 | 16 | 729.1 | 0.1138 | 1 | 0
DOVE/SD | 0.166 | 9999 | 556.5 | 0.919 | 1 | 26/7 | 0.1613 | 22600 | 0.5083 | 13 | 765 | 0.1138 | 1 | 0
DOVE/T2 | 0.0828 | 0.0995 | 1112 | 1.517 | 1 | 26/7 | 0.1463 | 45200 | 1.0166 | 16 | 1532 | 0.1138 | 1 | 0
DOVE/TW | 0.1628 | 0.1953 | 556.5 | 0.852 | 1 | 20/7 | 0.1668 | 22600 | 0.5083 | 12 | 764.5 | 0.1138 | 1 | 0
FALCON/TW | 0.0598 | 0.0709 | 1590 | 1.408 | 1 | 42/19 | 0.1946 | 55100 | 1.4071 | 18 | 2040 | 0.103 | 1 | 0
CURLEW/AW | 0.0887 | 0.1054 | 1033.5 | 1.245 | 1 | 54/7 | 0.1383 | 35200 | 0.9163 | 24 | 1275 | 0.1383 | 1 | 0
GOOSE | 0.146 | 9999 | 636 | 0.977 | 1 | 54/7 | 0.1085 | 23600 | 0.5642 | 24 | 819 | 0.1085 | 1 | 0
DRAKE/AW | 0.1129 | 0.1346 | 795 | 1.108 | 1 | 26/7 | 0.1749 | 30500 | 0.7264 | 16 | 1042 | 0.136 | 1 | 0
DRAKE/SD | 0.117 | 9999 | 795 | 1.077 | 1 | 26/7 | 0.1926 | 31800 | 0.7261 | 13 | 1093 | 0.136 | 1 | 0
DRAKE/TW | 0.1144 | 0.137 | 795 | 1.01 | 1 | 20/7 | 0.1994 | 31800 | 0.7261 | 12 | 1092 | 0.136 | 1 | 0
CURLEW | 0.091 | 0.108 | 1033.5 | 1.245 | 1 | 54/7 | 0.1383 | 36600 | 0.9163 | 24 | 1330 | 0.1383 | 1 | 0
CUMBERLAND/TW | 0.0501 | 0.0591 | 1926.9 | 1.545 | 1 | 42/19 | 0.2142 | 65300 | 1.7049 | 18 | 2471 | 0.1133 | 1 | 0
DUCK | 0.1533 | 9999 | 606 | 0.953 | 1 | 54/7 | 0.1059 | 22500 | 0.5379 | 24 | 779 | 0.1059 | 1 | 0
EAGLE | 0.164 | 0.196 | 556.5 | 0.953 | 1 | 30/7 | 0.1362 | 27800 | 0.5391 | 18 | 871.9 | 0.1362 | 1 | 0
EAGLE/AW | 0.157 | 0.1875 | 556.5 | 0.953 | 1 | 30/7 | 0.1362 | 26800 | 0.5391 | 18 | 819 | 0.1362 | 1 | 0
EGRET | 0.144 | 0.172 | 636 | 1.019 | 1 | 30/19 | 0.1456 | 31500 | 0.6135 | 18 | 988.2 | 0.0874 | 1 | 0
EGRET/AW | 0.1378 | 0.1646 | 636 | 1.019 | 1 | 30/19 | 0.1456 | 29900 | 0.6135 | 18 | 928.9 | 0.0874 | 1 | 0
FALCON | 0.0611 | 0.0721 | 1590 | 1.545 | 1 | 54/19 | 0.1716 | 54500 | 1.407 | 24 | 2044 | 0.105 | 1 | 0
CURLEW/SD | 0.091 | 9999 | 1033.5 | 1.191 | 1 | 54/7 | 0.2129 | 36300 | 0.9169 | 14 | 1329 | 0.1383 | 1 | 0
KETTLE/TW | 0.0976 | 0.1166 | 957.2 | 1.06 | 1 | 32/7 | 0.173 | 26000 | 0.8038 | 14 | 1079 | 0.0973 | 1 | 0
IBIS/AW | 0.2239 | 0.2678 | 397 | 0.783 | 1 | 26/7 | 0.1236 | 15800 | 0.3627 | 16 | 520.3 | 0.0961 | 1 | 0
IBIS/SD | 0.231 | 9999 | 397.5 | 0.771 | 1 | 26/7 | 0.1138 | 16400 | 0.3627 | 14 | 546.5 | 0.0961 | 1 | 0
IBIS/T2 | 0.1154 | 0.1371 | 795 | 1.282 | 1 | 26/7 | 0.1236 | 32600 | 0.725 | 16 | 1093 | 0.0961 | 1 | 0
CONDOR/SD | 0.117 | 9999 | 795 | 1.055 | 1 | 54/7 | 0.2018 | 28200 | 0.7053 | 12 | 1023 | 0.1213 | 1 | 0
CONDOR/AW | 0.1142 | 0.1361 | 795 | 1.092 | 1 | 54/7 | 0.1213 | 27800 | 0.7049 | 24 | 981.3 | 0.1213 | 1 | 0
RAVEN/AW | 0.8304 | 0.9938 | 105.7 | 0.398 | 1 | 6/1 | 0.1327 | 4380 | 0.0968 | 6 | 138.2 | 0.1327 | 1 | 0
JAEGER/T2 | 0.1986 | 0.2222 | 456.4 | 0.922 | 1 | 18/1 | 0.1126 | 12200 | 0.3784 | 12 | 495.4 | 0.1126 | 1 | 0
JAMES/TW | 0.0553 | 0.0654 | 1730.6 | 1.47 | 1 | 34/19 | 0.2256 | 59400 | 1.5314 | 14 | 2221 | 0.1075 | 1 | 0
JOREE | 0.0428 | 0.0491 | 2515 | 1.88 | 1 | 76/19 | 0.1819 | 61700 | 2.0826 | 28 | 2749 | 0.0849 | 1 | 0
JOREE/AW | 0.0424 | 0.0489 | 2515 | 1.88 | 1 | 76/19 | 0.1819 | 60600 | 2.0826 | 28 | 2693 | 0.0849 | 1 | 0
JUNCO | 0.342 | 9999 | 266.8 | 0.66 | 1 | 30/7 | 0.0943 | 13700 | 0.2589 | 18 | 418 | 0.0943 | 1 | 0
CRANE/AW | 0.1041 | 0.124 | 874.5 | 1.146 | 1 | 54/7 | 0.1273 | 30600 | 0.7766 | 24 | 1081 | 0.1273 | 1 | 0
COLUMBIA/TW | 0.0949 | 0.1136 | 966.2 | 1.092 | 1 | 21/7 | 0.2145 | 34000 | 0.8573 | 13 | 1241 | 0.1338 | 1 | 0
HUDSON/TW | 0.0794 | 0.0948 | 1158.4 | 1.196 | 1 | 26/7 | 0.2111 | 39600 | 1.0281 | 16 | 1489 | 0.1467 | 1 | 0
KILLDEER/SD | 0.1484 | 9999 | 636 | 0.917 | 1 | 45/7 | 0.1838 | 17700 | 0.5341 | 19 | 715 | 0.0793 | 1 | 0
KINGBIRD | 0.147 | 0.175 | 636 | 0.94 | 1 | 18/1 | 0.188 | 15700 | 0.5275 | 12 | 690.8 | 0.188 | 1 | 0
KINGBIRD/AW | 0.1454 | 0.1735 | 636 | 0.94 | 1 | 18/1 | 0.188 | 15020 | 0.5275 | 12 | 676.5 | 0.188 | 1 | 0
KINGFISHER | 0.0447 | 9999 | 2385 | 1.82 | 1 | 72/7 | 0.182 | 54400 | 1.954 | 27 | 2535 | 0.1213 | 1 | 0
KINGFISHER/AW | 0.0439 | 9999 | 2385 | 1.82 | 1 | 72/7 | 0.182 | 54000 | 1.954 | 27 | 2475 | 0.1213 | 1 | 0
KINGLET/T2 | 0.0853 | 0.101 | 1113 | 1.455 | 1 | 20/7 | 0.1667 | 30500 | 0.9334 | 13 | 1252.6 | 0.0741 | 1 | 0
COCHIN | 0.418 | 0.692 | 211.3 | 0.664 | 1 | 12/7 | 0.1327 | 20700 | 0.2628 | 12 | 527.5 | 0.1327 | 1 | 0
KIWI | 0.0484 | 0.0562 | 2167 | 1.735 | 1 | 72/7 | 0.1735 | 49800 | 1.7758 | 27 | 2303 | 0.1157 | 1 | 0
KIWI/AW | 0.0481 | 0.0558 | 2167 | 1.735 | 1 | 72/7 | 0.1735 | 49130 | 1.7758 | 27 | 2265 | 0.1157 | 1 | 0
KIWI/SD | 0.0484 | 9999 | 2167 | 1.725 | 1 | 72/7 | 0.1917 | 50700 | 1.7758 | 24 | 2296 | 0.1157 | 1 | 0
CHUKAR/TW | 0.0545 | 0.0644 | 1780 | 1.445 | 1 | 37/19 | 0.2193 | 50700 | 1.512 | 17 | 2063 | 0.0874 | 1 | 0
CONDOR | 0.117 | 0.14 | 795 | 1.092 | 1 | 54/7 | 0.1213 | 28200 | 0.7049 | 24 | 1024 | 0.1213 | 1 | 0
GUINEA | 0.552 | 0.873 | 159 | 0.576 | 1 | 12/7 | 0.1151 | 16000 | 0.1977 | 12 | 396.9 | 0.1151 | 1 | 0
SPARROW/T2 | 0.7388 | 0.8799 | 132.7 | 0.517 | 1 | 6/1 | 0.1052 | 5700 | 0.1216 | 6 | 182.7 | 0.1052 | 1 | 0
GRACKLE | 0.0798 | 0.0947 | 1192.5 | 1.338 | 1 | 54/19 | 0.1486 | 41900 | 1.055 | 24 | 1533 | 0.0892 | 1 | 0
GRACKLE/AW | 0.0779 | 0.0924 | 1192.5 | 1.338 | 1 | 54/19 | 0.1486 | 40200 | 1.055 | 24 | 1471 | 0.0892 | 1 | 0
GRACKLE/SD | 0.0798 | 9999 | 1192.5 | 1.274 | 1 | 54/19 | 0.2138 | 41900 | 1.055 | 16 | 1526 | 0.0892 | 1 | 0
GRACKLE/TW | 0.0783 | 0.0934 | 1192.5 | 1.225 | 1 | 38/19 | 0.1771 | 41900 | 1.0554 | 16 | 1530 | 0.0892 | 1 | 0
GRAPE | 0.39 | 0.3846 | 284.19 | 0.689 | 1 | 30/7 | 0.0984 | 14320.3284 | 0.2815 | 18 | 453.5798 | 0.0984 | 1 | 0
GREBE | 0.1314 | 9999 | 715.5 | 1.009 | 1 | 45/7 | 0.1261 | 20600 | 0.6014 | 21 | 807 | 0.0841 | 1 | 0
GROSBEAK | 0.145 | 0.173 | 636 | 0.99 | 1 | 26/7 | 0.1564 | 25200 | 0.5808 | 16 | 875.2 | 0.1216 | 1 | 0
GROSBEAK/AW | 0.1406 | 0.1678 | 636 | 0.99 | 1 | 26/7 | 0.1564 | 24800 | 0.5808 | 16 | 833 | 0.1216 | 1 | 0
GROSBEAK/SD | 0.145 | 9999 | 636 | 0.975 | 1 | 26/7 | 0.1723 | 25400 | 0.5808 | 13 | 874 | 0.1216 | 1 | 0
GROSBEAK/TW | 0.1426 | 0.171 | 636 | 0.908 | 1 | 20/7 | 0.1783 | 25400 | 0.5808 | 12 | 873.5 | 0.1216 | 1 | 0
IBIS | 0.231 | 0.277 | 397.5 | 0.783 | 1 | 26/7 | 0.1236 | 16300 | 0.3627 | 16 | 546.6 | 0.0961 | 1 | 0
CORNCRAKE | 0.099 | 0.118 | 954 | 1.165 | 1 | 20/7 | 0.2184 | 25600 | 0.801 | 13 | 1075 | 0.0971 | 1 | 0
CONDOR/TW | 0.1147 | 0.1373 | 795 | 0.993 | 1 | 20/7 | 0.1994 | 28200 | 0.7053 | 12 | 1021 | 0.1213 | 1 | 0
GULL | 0.139 | 9999 | 666.6 | 1 | 1 | 54/7 | 0.1111 | 24500 | 0.5921 | 24 | 858 | 0.1111 | 1 | 0
HAWK | 0.193 | 0.231 | 477 | 0.858 | 1 | 26/7 | 0.1354 | 19500 | 0.4354 | 16 | 656 | 0.1053 | 1 | 0
HAWK/AW | 0.1869 | 0.2233 | 477 | 0.858 | 1 | 26/7 | 0.1354 | 19000 | 0.4354 | 16 | 624.5 | 0.1053 | 1 | 0
HAWK/SD | 0.193 | 9999 | 477 | 0.86 | 1 | 26/7 | 0.1496 | 19500 | 0.4356 | 13 | 655.8 | 0.1053 | 1 | 0
HAWK/T2 | 0.0967 | 0.1147 | 954 | 1.405 | 1 | 26/7 | 0.1354 | 39000 | 0.8712 | 16 | 1311.9 | 0.1053 | 1 | 0
HAWK/TW | 0.1878 | 0.2277 | 477 | 0.789 | 1 | 18/7 | 0.1628 | 19400 | 0.4356 | 10 | 655 | 0.1053 | 1 | 0
CORN | 0.39 | 0.3846 | 284.19 | 0.689 | 1 | 30/7 | 0.0984 | 13848.2297 | 0.2815 | 18 | 453.5798 | 0.0984 | 1 | 0
HEN | 0.191 | 0.229 | 477 | 0.883 | 1 | 30/7 | 0.1261 | 23800 | 0.4621 | 18 | 747.4 | 0.1261 | 1 | 0
HEN/AW | 0.1829 | 0.2185 | 477 | 0.883 | 1 | 30/7 | 0.1261 | 23400 | 0.4621 | 18 | 702 | 0.1261 | 1 | 0
HEN/T2 | 0.0956 | 0.1139 | 954 | 1.445 | 1 | 30/7 | 0.1261 | 47600 | 0.624 | 18 | 1494.2 | 0.1261 | 1 | 0
COOT | 0.119 | 0.142 | 795 | 1.04 | 1 | 36/1 | 0.1486 | 16800 | 0.6416 | 18 | 804.7 | 0.1486 | 1 | 0
CRANE | 0.107 | 0.127 | 874.5 | 1.146 | 1 | 54/7 | 0.1273 | 31400 | 0.7766 | 24 | 1126 | 0.1273 | 1 | 0
GROUSE | 1.114 | 1.38 | 80 | 0.367 | 1 | 8/1 | 0.1 | 5200 | 0.0847 | 8 | 149 | 0.167 | 1 | 0
OXBIRD/SD | 0.0817 | 9999 | 1192.5 | 1.266 | 1 | 42/7 | 0.1582 | 29500 | 0.9848 | 21 | 1286 | 0.0936 | 1 | 0
MONONGAHELA/TW | 0.2258 | 0.2709 | 405.1 | 0.681 | 1 | 14/1 | 0.1701 | 10200 | 0.3362 | 9 | 441 | 0.152 | 1 | 0
BLUEJAY | 0.0859 | 0.102 | 1113 | 1.258 | 1 | 45/7 | 0.1573 | 29800 | 0.935 | 21 | 1255 | 0.1049 | 1 | 0
MOOSE | 0.1061 | 0.1112 | 1017.94 | 1.251 | 1 | 54/7 | 0.139 | 35870.5119 | 0.8975 | 24 | 1344.8808 | 0.139 | 1 | 0
BANANA | 0.8578 | 0.9447 | 128.48 | 0.445 | 1 | 6/1 | 0.1476 | 5126 | 0.1198 | 6 | 180.1 | 0.1476 | 1 | 0
PLOVER/TW | 0.0659 | 0.0784 | 1431 | 1.337 | 1 | 37/19 | 0.1967 | 49600 | 1.2664 | 17 | 1836 | 0.0977 | 1 | 0
PLOVER/SD | 0.0673 | 9999 | 1431 | 1.448 | 1 | 54/19 | 0.1609 | 49600 | 1.267 | 24 | 1835 | 0.0977 | 1 | 0
PLATTE/TW | 0.0617 | 0.073 | 1569 | 1.334 | 1 | 33/7 | 0.218 | 38200 | 1.2957 | 15 | 1693 | 0.1074 | 1 | 0
PLOVER/AW | 0.0658 | 0.0777 | 1431 | 1.465 | 1 | 54/19 | 0.1628 | 47700 | 1.267 | 24 | 1766 | 0.0977 | 1 | 0
PENGUIN | 0.434 | 0.611 | 211.6 | 0.563 | 1 | 6/1 | 0.1878 | 8350 | 0.1939 | 6 | 291.1 | 0.1878 | 1 | 0
PENGUIN/AW | 0.4149 | 0.4965 | 211.6 | 0.563 | 1 | 6/1 | 0.1878 | 8350 | 0.1939 | 6 | 276.8 | 0.1878 | 1 | 0
MYSTIC/TW | 0.1367 | 0.1638 | 666.6 | 0.913 | 1 | 20/7 | 0.1826 | 24000 | 0.5914 | 12 | 856.3 | 0.1111 | 1 | 0
OSWEGO/TW | 0.1364 | 0.1635 | 664.8 | 0.927 | 1 | 20/7 | 0.1823 | 26600 | 0.6072 | 12 | 913.4 | 0.1244 | 1 | 0
PENGUIN/T2 | 0.2586 | 0.2999 | 423.2 | 0.922 | 1 | 6/1 | 0.1878 | 16700 | 0.3878 | 6 | 582.1 | 0.1878 | 1 | 0
OSTRICH/AW | 0.2962 | 0.3543 | 300 | 0.68 | 1 | 26/7 | 0.1074 | 12100 | 0.2744 | 16 | 392.9 | 0.0835 | 1 | 0
PARTRIDGE/T2 | 0.1706 | 0.2032 | 533.6 | 1.051 | 1 | 26/7 | 0.1013 | 22600 | 0.487 | 16 | 734 | 0.0788 | 1 | 0
SPARROW | 1.368 | 1.774 | 66.36 | 0.316 | 1 | 6/1 | 0.1052 | 2850 | 0.0608 | 6 | 91.3 | 0.1052 | 1 | 0
OXBIRD/TW | 0.0794 | 0.0945 | 1192.5 | 1.167 | 1 | 30/7 | 0.1994 | 29500 | 0.9848 | 14 | 1286 | 0.0936 | 1 | 0
MIRAMICHI/TW | 0.0658 | 0.078 | 1455.3 | 1.302 | 1 | 36/7 | 0.2011 | 39200 | 1.2222 | 16 | 1640 | 0.12 | 1 | 0
MERRIMACK/TW | 0.0658 | 0.0782 | 1433.6 | 1.34 | 1 | 39/19 | 0.1917 | 49700 | 1.2677 | 17 | 1840 | 0.0978 | 1 | 0
MILLET | 0.199 | 0.1963 | 556.53 | 0.965 | 1 | 30/7 | 0.1378 | 26077.8351 | 0.5518 | 18 | 887.0004 | 0.1378 | 1 | 0
BLUEBIRD/TW | 0.0465 | 0.0544 | 2156 | 1.608 | 1 | 64/19 | 0.1836 | 61100 | 1.8321 | 22 | 2515 | 0.0961 | 1 | 0
MINK | 0.8994 | 1.0235 | 122.75 | 0.432 | 1 | 6/1 | 0.1441 | 4860 | 0.114 | 6 | 171 | 0.1441 | 1 | 0
ORTOLAN/TW | 0.0906 | 0.1081 | 1033.5 | 1.102 | 1 | 32/7 | 0.1797 | 28100 | 0.8673 | 14 | 1165 | 0.101 | 1 | 0
MINORCA | 0.787 | 1.179 | 110.8 | 0.48 | 1 | 12/7 | 0.0961 | 11300 | 0.1378 | 12 | 276.6 | 0.0961 | 1 | 0
POWDER/TW | 0.0464 | 0.0543 | 2153.8 | 1.602 | 1 | 64/19 | 0.1834 | 61100 | 1.829 | 22 | 2498 | 0.0961 | 1 | 0
MOHAWK/TW | 0.159 | 0.1907 | 571.7 | 0.846 | 1 | 18/7 | 0.1782 | 20700 | 0.5074 | 10 | 734.7 | 0.103 | 1 | 0
BITTERN/SD | 0.0759 | 9999 | 1272 | 1.323 | 1 | 45/7 | 0.1653 | 34600 | 1.068 | 21 | 1433 | 0.1121 | 1 | 0
POPINJAY/SD | 0.069 | 9999 | 1431 | 1.381 | 1 | 42/7 | 0.1726 | 35300 | 1.179 | 21 | 1544 | 0.1025 | 1 | 0
BITTERN/TW | 0.0745 | 0.0885 | 1272 | 1.22 | 1 | 35/7 | 0.1906 | 34600 | 1.0681 | 16 | 1433 | 0.1121 | 1 | 0
POTOMAC/TW | 0.0617 | 0.0731 | 1557.4 | 1.345 | 1 | 36/7 | 0.208 | 41900 | 1.3079 | 16 | 1755 | 0.1241 | 1 | 0
PELICAN/T2 | 0.0989 | 0.1174 | 954 | 1.333 | 1 | 18/1 | 0.1628 | 23600 | 0.7908 | 12 | 1035.7 | 0.1628 | 1 | 0
BITTERN | 0.0759 | 0.0898 | 1272 | 1.345 | 1 | 45/7 | 0.1681 | 34100 | 1.068 | 21 | 1434 | 0.1121 | 1 | 0
POTATO | 0.0939 | 0.1014 | 1150.56 | 1.331 | 1 | 54/19 | 0.1476 | 39791.1795 | 1.0411 | 24 | 1511.9325 | 0.0886 | 1 | 0
BALDPATE | 0.1024 | 9999 | 900 | 1.212 | 1 | 30/7 | 0.1732 | 43300 | 0.8711 | 18 | 1410 | 0.1732 | 1 | 0
NECHAKO/TW | 0.1214 | 0.1451 | 768.9 | 0.93 | 1 | 27/1 | 0.1688 | 16400 | 0.622 | 13 | 781.9 | 0.152 | 1 | 0
BITTERN/AW | 0.0749 | 0.0886 | 1272 | 1.345 | 1 | 45/7 | 0.1681 | 33400 | 1.068 | 21 | 1398 | 0.1121 | 1 | 0
PHEASANT/TW | 0.0736 | 0.0876 | 1272 | 1.264 | 1 | 39/19 | 0.1806 | 44100 | 1.1256 | 17 | 1632 | 0.0921 | 1 | 0
PETREL | 0.858 | 1.264 | 101.8 | 0.461 | 1 | 12/7 | 0.0921 | 10400 | 0.1265 | 12 | 254.1 | 0.0921 | 1 | 0
OSPREY/AW | 0.1658 | 0.198 | 556.5 | 0.879 | 1 | 18/1 | 0.1758 | 13200 | 0.4612 | 12 | 591.6 | 0.1758 | 1 | 0
OSPREY | 0.168 | 0.2 | 556.5 | 0.879 | 1 | 18/1 | 0.1758 | 13700 | 0.4612 | 12 | 604.1 | 0.1758 | 1 | 0
PHOEBE | 0.309 | 9999 | 300 | 0.646 | 1 | 18/1 | 0.1291 | 7700 | 0.248 | 12 | 326 | 0.1291 | 1 | 0
ORIOLE/AW | 0.2588 | 0.3094 | 336.4 | 0.741 | 1 | 30/7 | 0.1059 | 17300 | 0.3259 | 18 | 495.1 | 0.1059 | 1 | 0
ORTOLAN | 0.0922 | 0.11 | 1033.5 | 1.212 | 1 | 45/7 | 0.1515 | 27700 | 0.8673 | 21 | 1164 | 0.101 | 1 | 0
PLOVER | 0.0673 | 0.0796 | 1431 | 1.465 | 1 | 54/19 | 0.1628 | 49100 | 1.267 | 24 | 1840 | 0.0977 | 1 | 0
BEAN | 1.3412 | 1.4371 | 82.49 | 0.354 | 1 | 6/1 | 0.1181 | 3260 | 0.0767 | 6 | 114.9 | 0.1181 | 1 | 0
PHOENIX/SD | 0.1001 | 9999 | 954 | 1.088 | 1 | 42/7 | 0.2178 | 23700 | 0.7877 | 13 | 1027 | 0.0836 | 1 | 0
PHEASANT/SD | 0.0751 | 9999 | 1272 | 1.378 | 1 | 54/19 | 0.1723 | 44100 | 1.126 | 21 | 1632 | 0.0921 | 1 | 0
BLUEBIRD | 0.0477 | 0.0555 | 2156 | 1.762 | 1 | 84/19 | 0.1602 | 60300 | 1.8309 | 30 | 2511 | 0.0961 | 1 | 0
BEAR | 0.2169 | 0.2205 | 510.15 | 0.924 | 1 | 30/7 | 0.1319 | 24953.7905 | 0.5063 | 18 | 818.7954 | 0.1319 | 1 | 0
PHEASANT | 0.0751 | 0.089 | 1272 | 1.382 | 1 | 54/19 | 0.1535 | 43600 | 1.126 | 24 | 1635 | 0.0921 | 1 | 0
ORTOLAN/AW | 0.0909 | 0.1079 | 1033.5 | 1.212 | 1 | 45/7 | 0.1515 | 27200 | 0.8673 | 21 | 1135 | 0.101 | 1 | 0
PHEASANT/AW | 0.0733 | 0.0869 | 1272 | 1.382 | 1 | 54/19 | 0.1535 | 42400 | 1.126 | 24 | 1570 | 0.0921 | 1 | 0
ORTOLAN/SD | 0.0922 | 9999 | 1033.5 | 1.145 | 1 | 45/7 | 0.2167 | 28100 | 0.8678 | 14 | 1161 | 0.101 | 1 | 0
BARLEY | 1.9315 | 2.039 | 57.23 | 0.295 | 1 | 6/1 | 0.0984 | 2316 | 0.0533 | 6 | 80 | 0.0984 | 1 | 0
OLIVE | 0.1079 | 0.1154 | 1002.55 | 1.24 | 1 | 54/7 | 0.1378 | 35744.6189 | 0.9097 | 24 | 1317.0612 | 0.1378 | 1 | 0
NELSON/TW | 0.0753 | 0.0895 | 1257.1 | 1.213 | 1 | 35/7 | 0.1895 | 34200 | 1.0557 | 16 | 1417 | 0.1115 | 1 | 0
BLUEBIRD/SD | 0.0477 | 9999 | 2156 | 1.716 | 1 | 84/19 | 0.2145 | 60700 | 1.8311 | 21 | 2504 | 0.0961 | 1 | 0
NUTHATCH | 0.0649 | 0.0765 | 1510.5 | 1.465 | 1 | 45/7 | 0.1832 | 40100 | 1.268 | 21 | 1703 | 0.1221 | 1 | 0
PIPIT/SD | 0.1489 | 9999 | 636 | 0.894 | 1 | 42/7 | 0.1932 | 15600 | 0.5252 | 11 | 684 | 0.0684 | 1 | 0
NUTHATCH/AW | 0.0641 | 0.0755 | 1510.5 | 1.465 | 1 | 45/7 | 0.1832 | 39700 | 1.268 | 21 | 1660 | 0.1221 | 1 | 0
PIPER | 0.304 | 9999 | 300 | 0.7 | 1 | 30/7 | 0.1 | 15500 | 0.2899 | 18 | 470 | 0.1 | 1 | 0
PIGEON/T2 | 0.3106 | 0.34 | 335.6 | 0.822 | 1 | 6/1 | 0.1672 | 13240 | 0.3076 | 6 | 461.4 | 0.1672 | 1 | 0
BISON | 0.1474 | 0.1569 | 733.75 | 1.062 | 1 | 54/7 | 0.1181 | 26201.48 | 0.6671 | 24 | 969.5855 | 0.1181 | 1 | 0
OATS | 0.1468 | 0.153 | 736.12 | 1.063 | 1 | 54/7 | 0.1181 | 25853.0262 | 0.6684 | 24 | 967.6368 | 0.1181 | 1 | 0
ORIOLE | 0.271 | 0.324 | 336.4 | 0.741 | 1 | 30/7 | 0.1059 | 17300 | 0.3259 | 18 | 527.1 | 0.1059 | 1 | 0
ONION | 0.1251 | 0.1321 | 864.4 | 1.154 | 1 | 54/7 | 0.128 | 29675 | 0.7843 | 24 | 1135.6 | 0.128 | 1 | 0
BLUEBIRD/AW | 0.0471 | 0.0548 | 2156 | 1.762 | 1 | 84/19 | 0.1602 | 59000 | 1.8309 | 30 | 2439 | 0.0961 | 1 | 0
OSTRICH | 0.306 | 0.366 | 300 | 0.68 | 1 | 26/7 | 0.1074 | 12700 | 0.2744 | 16 | 413 | 0.0835 | 1 | 0
OSPREY/T2 | 0.0856 | 0.1013 | 1113 | 1.439 | 1 | 18/1 | 0.1758 | 27400 | 0.9228 | 12 | 1207.7 | 0.1758 | 1 | 0
ORANGE | 0.1251 | 0.1321 | 864.4 | 1.154 | 1 | 54/7 | 0.128 | 30798.8225 | 0.7843 | 24 | 1135.6293 | 0.128 | 1 | 0
PHOENIX/TW | 0.0982 | 0.1172 | 954 | 1.044 | 1 | 30/7 | 0.1783 | 23700 | 0.7876 | 14 | 1032 | 0.0837 | 1 | 0
PELICAN/AW | 0.1916 | 0.2294 | 477 | 0.814 | 1 | 18/1 | 0.1628 | 11500 | 0.3955 | 12 | 507.2 | 0.1628 | 1 | 0
PIGEON | 0.546 | 0.763 | 167.8 | 0.502 | 1 | 6/1 | 0.1672 | 6620 | 0.1537 | 6 | 230.8 | 0.1672 | 1 | 0
RAIL | 0.0994 | 0.118 | 954 | 1.165 | 1 | 45/7 | 0.1456 | 25900 | 0.801 | 21 | 1076 | 0.0971 | 1 | 0
ATHABASKA/TW | 0.0506 | 0.0595 | 1949.6 | 1.504 | 1 | 42/7 | 0.2155 | 51900 | 1.6377 | 18 | 2199 | 0.1392 | 1 | 0
RAIL/SD | 0.0994 | 9999 | 954 | 1.103 | 1 | 45/7 | 0.2163 | 26100 | 0.8011 | 13 | 1073 | 0.0971 | 1 | 0
RAIL/AW | 0.0981 | 0.1167 | 954 | 1.165 | 1 | 45/7 | 0.1456 | 25400 | 0.801 | 21 | 1049 | 0.0971 | 1 | 0
BOBOLINK/SD | 0.0681 | 9999 | 1431 | 1.398 | 1 | 45/7 | 0.1747 | 38900 | 1.202 | 21 | 1612 | 0.1189 | 1 | 0
BOBOLINK/AW | 0.0673 | 0.0794 | 1431 | 1.427 | 1 | 45/7 | 0.1783 | 37600 | 1.201 | 21 | 1572 | 0.1189 | 1 | 0
PEACOCK/AW | 0.1493 | 0.1783 | 605 | 0.953 | 1 | 24/7 | 0.1588 | 21000 | 0.537 | 15 | 747.7 | 0.1059 | 1 | 0
RAIL/TW | 0.0979 | 0.116 | 954 | 1.061 | 1 | 32/7 | 0.1727 | 25900 | 0.8011 | 14 | 1075 | 0.0971 | 1 | 0
PARSNIP | 0.1079 | 0.1154 | 1002.55 | 1.24 | 1 | 54/7 | 0.1378 | 34395.7653 | 0.9097 | 24 | 1317.0612 | 0.1378 | 1 | 0
BRAHMA | 0.417 | 0.712 | 203.2 | 0.714 | 1 | 16/19 | 0.1127 | 28400 | 0.302 | 16 | 676.9 | 0.0977 | 1 | 0
BOBOLINK | 0.0681 | 0.0804 | 1431 | 1.427 | 1 | 45/7 | 0.1783 | 38300 | 1.201 | 21 | 1613 | 0.1189 | 1 | 0
WIDGEON | 0.2749 | 9999 | 336.4 | 0.71 | 1 | 24/7 | 0.1184 | 12500 | 0.2992 | 15 | 433 | 0.0788 | 1 | 0
PARROT/AW | 0.0624 | 0.0737 | 1510.5 | 1.505 | 1 | 54/19 | 0.1672 | 50500 | 1.336 | 24 | 1862 | 0.1003 | 1 | 0
PANTHER | 0.2726 | 0.2704 | 407.53 | 0.826 | 1 | 30/7 | 0.1181 | 20059.7003 | 0.4046 | 18 | 654.4316 | 0.1181 | 1 | 0
BLUEJAY/T2 | 0.043 | 9999 | 2226 | 2.059 | 1 | 45/7 | 0.1573 | 59600 | 1.87 | 45 | 2510 | 0.1049 | 1 | 0
MARTIN | 0.071 | 0.084 | 1351.5 | 1.424 | 1 | 54/19 | 0.1582 | 46300 | 1.196 | 24 | 1737 | 0.0949 | 1 | 0
PARTRIDGE | 0.344 | 0.411 | 266.8 | 0.642 | 1 | 26/7 | 0.1013 | 11300 | 0.2436 | 16 | 367.3 | 0.0788 | 1 | 0
WOODDUCK | 0.1514 | 9999 | 605 | 0.994 | 1 | 30/7 | 0.142 | 29400 | 0.5828 | 18 | 940 | 0.142 | 1 | 0
WILLET | 0.1082 | 9999 | 874.5 | 1.115 | 1 | 45/7 | 0.1394 | 25000 | 0.7347 | 21 | 987 | 0.0929 | 1 | 0
WOLF | 0.3642 | 0.3589 | 304.51 | 0.714 | 1 | 30/7 | 0.102 | 15170.1062 | 0.3023 | 18 | 488.9254 | 0.102 | 1 | 0
RAVEN | 0.862 | 1.141 | 105.6 | 0.398 | 1 | 6/1 | 0.1327 | 4380 | 0.0968 | 6 | 145.3 | 0.1327 | 1 | 0
PARTRIDGE/SD | 0.344 | 9999 | 266.8 | 0.645 | 1 | 26/7 | 0.1256 | 11350 | 0.2436 | 12 | 367 | 0.0788 | 1 | 0
PARTRIDGE/AW | 0.3328 | 0.3981 | 266.8 | 0.642 | 1 | 26/7 | 0.1013 | 10800 | 0.2436 | 16 | 349.6 | 0.0788 | 1 | 0
PAWPAW | 0.0939 | 0.1014 | 1150.56 | 1.331 | 1 | 54/19 | 0.1476 | 40240.7973 | 1.0411 | 24 | 1511.9325 | 0.0886 | 1 | 0
BOBOLINK/TW | 0.0668 | 0.0792 | 1431 | 1.291 | 1 | 36/7 | 0.1994 | 38900 | 1.2017 | 16 | 1613 | 0.1189 | 1 | 0
APPLE | 1.3304 | 1.4371 | 82.49 | 0.354 | 1 | 6/1 | 0.1181 | 3350 | 0.0767 | 6 | 114.9 | 0.1181 | 1 | 0
BLUEJAY/TW | 0.0845 | 0.1005 | 1113 | 1.143 | 1 | 33/7 | 0.1836 | 30300 | 0.9347 | 15 | 1257 | 0.1049 | 1 | 0
YUKON/TW | 0.0758 | 0.0903 | 1233.6 | 1.245 | 1 | 38/19 | 0.1802 | 42900 | 1.0925 | 16 | 1586 | 0.091 | 1 | 0
ZEBRA | 0.1311 | 0.1291 | 823.55 | 1.125 | 1 | 54/7 | 0.1252 | 29252.1371 | 0.7486 | 24 | 1087.8522 | 0.1252 | 1 | 0
PEACH | 0.0587 | 0.0666 | 1847.21 | 1.685 | 1 | 54/19 | 0.187 | 63845.7343 | 1.6709 | 24 | 2419.092 | 0.1122 | 1 | 0
COYOTE | 0.3637 | 0.4297 | 260.7 | 0.626 | 1 | 26/7 | 0.1 | 10600 | 0.2359 | 16 | 350.4 | 0.0752 | 1 | 0
BRANT | 0.2327 | 9999 | 397.5 | 0.772 | 1 | 24/7 | 0.1287 | 14600 | 0.3527 | 15 | 512.1 | 0.0858 | 1 | 0
PEACOCK | 0.153 | 0.183 | 605 | 0.953 | 1 | 24/7 | 0.1588 | 21600 | 0.537 | 15 | 779.7 | 0.1059 | 1 | 0
ALMOND | 1.9315 | 2.039 | 57.23 | 0.295 | 1 | 6/1 | 0.0984 | 2360 | 0.0533 | 6 | 80 | 0.0984 | 1 | 0
MERLIN/T2 | 0.1384 | 0.1649 | 672.6 | 1.12 | 1 | 18/1 | 0.1367 | 17400 | 0.5578 | 12 | 730.3 | 0.1367 | 1 | 0
BLUEJAY/SD | 0.0859 | 9999 | 1113 | 1.243 | 1 | 45/7 | 0.1553 | 30300 | 0.935 | 21 | 1254 | 0.1049 | 1 | 0
BLUEJAY/AW | 0.0848 | 0.1006 | 1113 | 1.258 | 1 | 45/7 | 0.1573 | 29300 | 0.935 | 21 | 1224 | 0.1049 | 1 | 0
PARROT | 0.0641 | 0.0757 | 1510.5 | 1.505 | 1 | 54/19 | 0.1672 | 51700 | 1.336 | 24 | 1940 | 0.1003 | 1 | 0
PECOS/TW | 0.0585 | 0.069 | 1622 | 1.424 | 1 | 39/19 | 0.2039 | 57500 | 1.4429 | 17 | 2107 | 0.1064 | 1 | 0
MERLIN | 0.276 | 0.33 | 336.4 | 0.684 | 1 | 18/1 | 0.1367 | 8680 | 0.2789 | 12 | 365.2 | 0.1367 | 1 | 0
MERLIN/AW | 0.2726 | 0.3261 | 336.4 | 0.684 | 1 | 18/1 | 0.1367 | 8540 | 0.2789 | 12 | 357.6 | 0.1367 | 1 | 0
MAUMEE/TW | 0.1189 | 0.1424 | 768.2 | 0.977 | 1 | 20/7 | 0.196 | 27700 | 0.6819 | 12 | 987.8 | 0.1195 | 1 | 0
PARAKEET/AW | 0.1621 | 0.1936 | 556.5 | 0.914 | 1 | 24/7 | 0.1523 | 19300 | 0.4938 | 15 | 687.5 | 0.1015 | 1 | 0
MERGANSER | 0.0966 | 9999 | 954 | 1.248 | 1 | 30/7 | 0.1785 | 46000 | 0.9238 | 18 | 1493 | 0.1785 | 1 | 0
MERLIN/TW | 0.2715 | 9999 | 336.4 | 0.63 | 1 | 14/1 | 0.155 | 8560 | 0.2788 | 9 | 365 | 0.1367 | 1 | 0
PEE DEE/TW | 0.0554 | 0.0653 | 1758.6 | 1.427 | 1 | 37/7 | 0.1967 | 46700 | 1.477 | 17 | 1982 | 0.1319 | 1 | 0
PELICAN | 0.195 | 0.233 | 477 | 0.814 | 1 | 18/1 | 0.1628 | 11800 | 0.3955 | 12 | 518 | 0.1628 | 1 | 0
PUFFIN | 0.1179 | 9999 | 795 | 1.077 | 1 | 22/7 | 0.1901 | 24800 | 0.6857 | 14 | 958 | 0.1056 | 1 | 0
PTARMIGAN/T2 | 0.1174 | 0.1397 | 795 | 1.231 | 1 | 20/7 | 0.1401 | 22200 | 0.668 | 13 | 886.2 | 0.0626 | 1 | 0
PARAKEET | 0.166 | 0.199 | 556.5 | 0.914 | 1 | 24/7 | 0.1523 | 19800 | 0.4938 | 15 | 716.9 | 0.1015 | 1 | 0
PUFFIN/SD | 0.1179 | 9999 | 795 | 1.034 | 1 | 22/7 | 0.2033 | 25100 | 0.6857 | 12 | 956 | 0.1056 | 1 | 0
PARAKEET/T2 | 0.0841 | 0.0995 | 1113 | 1.496 | 1 | 24/7 | 0.1523 | 39600 | 0.9874 | 24 | 1434 | 0.1015 | 1 | 0
QUAIL/T2 | 0.3831 | 0.4599 | 266.2 | 0.732 | 1 | 6/1 | 0.1489 | 10600 | 0.2438 | 6 | 365.9 | 9999 | 1 | 0
MARTIN/TW | 0.0694 | 0.0826 | 1351.5 | 1.3 | 1 | 39/19 | 0.1862 | 46800 | 1.1959 | 17 | 1734 | 0.0949 | 1 | 0
AVOCET/TW | 0.0847 | 0.1009 | 1113 | 1.129 | 1 | 30/7 | 0.1926 | 27500 | 0.9191 | 14 | 1201 | 0.0904 | 1 | 0
PUFFIN/TW | 0.1152 | 0.138 | 795 | 0.98 | 1 | 18/7 | 0.2102 | 25900 | 0.6919 | 10 | 975.3 | 0.1108 | 1 | 0
PARAKEET/TW | 0.1633 | 0.1959 | 556.5 | 0.835 | 1 | 18/7 | 0.1758 | 20000 | 0.4937 | 10 | 714.9 | 0.1015 | 1 | 0
PARAKEET/SD | 0.166 | 9999 | 556.5 | 0.901 | 1 | 24/7 | 0.1622 | 20000 | 0.4938 | 13 | 716 | 0.1015 | 1 | 0
QUAIL | 0.687 | 0.929 | 133.1 | 0.447 | 1 | 6/1 | 0.149 | 5310 | 0.1221 | 6 | 183.2 | 0.149 | 1 | 0
RACOON | 0.7133 | 0.7403 | 153.54 | 0.483 | 1 | 6/1 | 0.161 | 6045 | 0.1425 | 6 | 213.8 | 0.161 | 1 | 0
MARTIN/AW | 0.0693 | 0.0821 | 1351 | 1.424 | 1 | 54/19 | 0.1582 | 46351 | 1.196 | 24 | 1667 | 0.0949 | 1 | 0
MARTIN/SD | 0.071 | 9999 | 1351.5 | 1.417 | 1 | 54/19 | 0.1772 | 46800 | 1.196 | 21 | 1733 | 0.0949 | 1 | 0
HUDSON/ACSS/TW | 0.079 | 0.0943 | 1158.4 | 1.196 | 2 | 26/7 | 0.2111 | 31100 | 1.0281 | 16 | 1489 | 0.1467 | 1 | 0
CONDOR/ACSS/TW | 0.1136 | 0.1361 | 795 | 0.993 | 2 | 20/7 | 0.1994 | 21700 | 0.7053 | 12 | 1021 | 0.1213 | 1 | 0
IBIS/ACSS/AW | 0.2179 | 0.2617 | 397.5 | 0.783 | 2 | 26/7 | 0.1236 | 12400 | 0.363 | 16 | 519.7 | 0.0961 | 1 | 0
IBIS/ACSS | 0.2249 | 0.2701 | 397.5 | 0.783 | 2 | 26/7 | 0.1236 | 13000 | 0.363 | 16 | 547 | 0.0961 | 1 | 0
PHEASANT/ACSS | 0.0732 | 0.0894 | 1272 | 1.382 | 2 | 54/19 | 0.1535 | 34100 | 1.126 | 24 | 1635 | 0.0921 | 1 | 0
CORNCRAKE/ACSS | 0.0968 | 0.1156 | 954 | 1.165 | 2 | 20/7 | 0.7492 | 16700 | 0.801 | 13 | 1074 | 0.0971 | 1 | 0
CONDOR/ACSS/AW | 0.1113 | 0.1372 | 795 | 1.092 | 2 | 54/7 | 0.1213 | 20900 | 0.7053 | 24 | 980.5 | 0.1213 | 1 | 0
PEE DEE/ACSS/TW | 0.0551 | 0.0666 | 1758.6 | 1.427 | 2 | 37/7 | 0.1967 | 30900 | 1.477 | 17 | 1982 | 0.1319 | 1 | 0
BITTERN/ACSS | 0.0739 | 0.0884 | 1272 | 1.345 | 2 | 45/7 | 0.1681 | 22300 | 1.068 | 21 | 1434 | 0.1121 | 1 | 0
HAWK/ACSS/AW | 0.1818 | 0.2183 | 477 | 0.858 | 2 | 26/7 | 0.1354 | 14900 | 0.4356 | 16 | 623.9 | 0.1053 | 1 | 0
PEACOCK/ACSS/AW | 0.1454 | 0.1744 | 605 | 0.953 | 2 | 24/7 | 0.1588 | 15900 | 0.5368 | 15 | 746.9 | 0.1059 | 1 | 0
HEN/ACSS/AW | 0.1782 | 0.2139 | 477 | 0.883 | 2 | 30/7 | 0.1261 | 20100 | 0.462 | 18 | 701.2 | 0.1261 | 1 | 0
BITTERN/ACSS/TW | 0.0737 | 0.0877 | 1272 | 1.22 | 2 | 35/7 | 0.1906 | 22300 | 1.0681 | 16 | 1433 | 0.1121 | 1 | 0
HEN/ACSS | 0.1863 | 0.2236 | 477 | 0.883 | 2 | 30/7 | 0.1261 | 21000 | 0.462 | 18 | 747 | 0.1261 | 1 | 0
HAWK/ACSS/TW | 0.187 | 0.2247 | 477 | 0.789 | 2 | 18/7 | 0.1628 | 15600 | 0.4356 | 10 | 655 | 0.1053 | 1 | 0
HAWK/ACSS | 0.1877 | 0.2253 | 477 | 0.858 | 2 | 26/7 | 0.1354 | 15600 | 0.4356 | 16 | 657 | 0.1053 | 1 | 0
BITTERN/ACSS/AW | 0.073 | 0.0872 | 1272 | 1.345 | 2 | 45/7 | 0.1681 | 21600 | 1.068 | 21 | 1395.9 | 0.1121 | 1 | 0
PEACOCK/ACSS | 0.149 | 0.1789 | 605 | 0.953 | 2 | 24/7 | 0.1588 | 16500 | 0.5368 | 15 | 780 | 0.1059 | 1 | 0
PECOS/ACSS/TW | 0.058 | 0.0688 | 1622 | 1.424 | 2 | 39/19 | 0.2039 | 45000 | 1.4429 | 17 | 2107 | 0.1064 | 1 | 0
JAMES/ACSS/TW | 0.0549 | 0.0649 | 1730.6 | 1.47 | 2 | 34/19 | 0.2256 | 46400 | 1.5314 | 14 | 2221 | 0.1075 | 1 | 0
CUCKOO/ACSS/AW | 0.1113 | 0.1333 | 795 | 1.092 | 2 | 24/7 | 0.182 | 20900 | 0.7053 | 15 | 980.9 | 0.1213 | 1 | 0
GANNET/ACSS/AW | 0.1307 | 0.1567 | 666.6 | 1.014 | 2 | 26/7 | 0.1601 | 20900 | 0.6037 | 16 | 872.2 | 0.1245 | 1 | 0
CURLEW/ACSS | 0.0886 | 0.1087 | 1033.5 | 1.245 | 2 | 54/7 | 0.1383 | 28200 | 0.9163 | 24 | 1330 | 0.1383 | 1 | 0
AVOCET/ACSS/TW | 0.0838 | 0.0999 | 1113 | 1.129 | 2 | 30/7 | 0.1926 | 16300 | 0.9191 | 14 | 1201 | 0.0904 | 1 | 0
EAGLE/ACSS/AW | 0.153 | 0.1835 | 556.5 | 0.953 | 2 | 30/7 | 0.1362 | 22900 | 0.5391 | 18 | 818.1 | 0.1362 | 1 | 0
EGRET/ACSS | 0.1402 | 0.1682 | 636 | 1.019 | 2 | 30/19 | 0.1456 | 28000 | 0.6135 | 18 | 988 | 0.0874 | 1 | 0
CURLEW/ACSS/TW | 0.0881 | 0.1053 | 1033.5 | 1.129 | 2 | 22/7 | 0.2167 | 28200 | 0.9169 | 13 | 1327 | 0.1383 | 1 | 0
CUMBERLAND/ACSS/TW | 0.0499 | 0.0588 | 1926.9 | 1.545 | 2 | 42/19 | 0.2142 | 51600 | 1.7049 | 18 | 2471 | 0.1133 | 1 | 0
RAIL/ACSS | 0.0968 | 0.1164 | 954 | 1.165 | 2 | 45/7 | 0.1456 | 16700 | 0.8011 | 21 | 1075 | 0.1456 | 1 | 0
FALCON/ACSS | 0.0596 | 0.0724 | 1590 | 1.545 | 2 | 54/19 | 0.1716 | 42600 | 1.407 | 24 | 2044 | 0.105 | 1 | 0
FALCON/ACSS/AW | 0.0583 | 0.0707 | 1590 | 1.545 | 2 | 54/19 | 0.1716 | 41100 | 1.407 | 24 | 1960 | 0.105 | 1 | 0
FALCON/ACSS/TW | 0.0592 | 0.0702 | 1590 | 1.408 | 2 | 42/19 | 0.1946 | 42600 | 1.4071 | 18 | 2038 | 0.103 | 1 | 0
PUFFIN/ACSS/TW | 0.1139 | 0.1365 | 795 | 0.98 | 2 | 18/7 | 0.2102 | 18900 | 0.6919 | 10 | 975.3 | 0.1108 | 1 | 0
PUFFIN/ACSS | 0.1147 | 0.1374 | 795 | 1.077 | 2 | 22/7 | 0.1901 | 17700 | 0.6857 | 14 | 956.4 | 0.1056 | 1 | 0
FINCH/ACSS | 0.083 | 0.1017 | 1113 | 1.293 | 2 | 54/19 | 0.1436 | 30400 | 0.9854 | 24 | 1431 | 0.0862 | 1 | 0
EGRET/ACSS/AW | 0.1343 | 0.161 | 636 | 1.019 | 2 | 30/19 | 0.1456 | 26300 | 0.6135 | 18 | 928.1 | 0.0874 | 1 | 0
DOVE/ACSS/TW | 0.1606 | 0.1928 | 556.5 | 0.852 | 2 | 20/7 | 0.1668 | 18200 | 0.5083 | 12 | 764.5 | 0.1138 | 1 | 0
RATITE/ACSS/AW | 0.0603 | 0.0711 | 1590 | 1.492 | 2 | 42/7 | 0.1946 | 22700 | 1.3134 | 20 | 1682.4 | 0.1081 | 1 | 0
DIPPER/ACSS | 0.0699 | 0.0835 | 1351.5 | 1.386 | 2 | 45/7 | 0.1733 | 23700 | 1.134 | 21 | 1523 | 0.1155 | 1 | 0
DIPPER/ACSS/AW | 0.0691 | 0.0824 | 1351.5 | 1.386 | 2 | 45/7 | 0.1733 | 23000 | 1.134 | 21 | 1483.3 | 0.1155 | 1 | 0
DIPPER/ACSS/TW | 0.0697 | 0.0828 | 1351.5 | 1.256 | 2 | 35/7 | 0.1965 | 23700 | 1.1348 | 16 | 1522 | 0.1155 | 1 | 0
RATITE/ACSS | 0.0608 | 0.0718 | 1590 | 1.492 | 2 | 42/7 | 0.1946 | 23400 | 1.3134 | 20 | 1715.6 | 0.1081 | 1 | 0
CURLEW/ACSS/AW | 0.0865 | 0.1061 | 1033.5 | 1.245 | 2 | 54/7 | 0.1383 | 26100 | 0.9163 | 24 | 1274.5 | 0.1383 | 1 | 0
DOVE/ACSS/AW | 0.1561 | 0.1873 | 556.5 | 0.927 | 2 | 26/7 | 0.1463 | 17500 | 0.5083 | 16 | 728.4 | 0.1138 | 1 | 0
PTARMIGAN/ACSS/AW | 0.2274 | 0.27 | 397.5 | 0.752 | 2 | 20/7 | 0.141 | 6760 | 0.3339 | 13 | 436.5 | 0.0627 | 1 | 0
ATHABASKA/ACSS/TW | 0.0505 | 0.0592 | 1949.6 | 1.504 | 2 | 42/7 | 0.2155 | 34300 | 1.6377 | 18 | 2199 | 0.1392 | 1 | 0
RAIL/ACSS/TW | 0.0967 | 0.1155 | 954 | 1.061 | 2 | 32/7 | 0.1727 | 16700 | 0.8011 | 14 | 1075 | 0.0971 | 1 | 0
DRAKE/ACSS | 0.1135 | 0.1359 | 795 | 1.108 | 2 | 26/7 | 0.1749 | 25900 | 0.7261 | 16 | 1094 | 0.136 | 1 | 0
DRAKE/ACSS/AW | 0.11 | 0.1318 | 795 | 1.108 | 2 | 26/7 | 0.1749 | 24400 | 0.7261 | 16 | 1040.8 | 0.136 | 1 | 0
DRAKE/ACSS/TW | 0.113 | 0.1355 | 795 | 1.01 | 2 | 20/7 | 0.1994 | 25900 | 0.7261 | 12 | 1092 | 0.136 | 1 | 0
RAIL/ACSS/AW | 0.0956 | 0.1149 | 954 | 1.165 | 2 | 45/7 | 0.1456 | 16200 | 0.8011 | 21 | 1047.2 | 0.1456 | 1 | 0
DOVE/ACSS | 0.161 | 0.1933 | 556.5 | 0.927 | 2 | 26/7 | 0.1463 | 18200 | 0.5083 | 16 | 766 | 0.1362 | 1 | 0
GRACKLE/ACSS/TW | 0.0773 | 0.0923 | 1192.5 | 1.225 | 2 | 38/19 | 0.1771 | 32600 | 1.0554 | 16 | 1530 | 0.0892 | 1 | 0
PLATTE/ACSS/TW | 0.0613 | 0.0724 | 1569 | 1.334 | 2 | 33/7 | 0.218 | 23100 | 1.2957 | 15 | 1693 | 0.1074 | 1 | 0
GENESEE/ACSS/TW | 0.0805 | 0.0959 | 1158 | 1.165 | 2 | 33/7 | 0.1873 | 20500 | 0.9733 | 15 | 1308 | 0.1078 | 1 | 0
PIPER/ACSS | 0.2956 | 0.355 | 300 | 0.7 | 2 | 30/7 | 0.1 | 13200 | 0.2899 | 18 | 470 | 0.1 | 1 | 0
GOLDFINCH/ACSS | 0.1426 | 0.1711 | 636 | 0.963 | 2 | 22/7 | 0.17 | 14100 | 0.5484 | 14 | 764.8 | 0.0944 | 1 | 0
GOLDFINCH/ACSS/AW | 0.14 | 0.1678 | 636 | 0.963 | 2 | 22/7 | 0.17 | 13600 | 0.5484 | 14 | 739.4 | 0.0944 | 1 | 0
FINCH/ACSS/AW | 0.081 | 0.0993 | 1113 | 1.293 | 2 | 54/19 | 0.1436 | 28800 | 0.9854 | 24 | 1372.6 | 0.0862 | 1 | 0
GRACKLE/ACSS/AW | 0.076 | 0.0929 | 1192.5 | 1.338 | 2 | 54/19 | 0.1486 | 30800 | 1.055 | 24 | 1469.9 | 0.0892 | 1 | 0
PLOVER/ACSS | 0.0656 | 0.0799 | 1431 | 1.465 | 2 | 54/19 | 0.1628 | 38400 | 1.267 | 24 | 1840 | 0.0977 | 1 | 0
PHOENIX/ACSS/TW | 0.097 | 0.1158 | 954 | 1.044 | 2 | 30/7 | 0.1783 | 14200 | 0.7876 | 14 | 1032 | 0.0837 | 1 | 0
GROSBEAK/ACSS | 0.1412 | 0.1694 | 636 | 0.99 | 2 | 26/7 | 0.1564 | 20800 | 0.5809 | 16 | 875 | 0.1216 | 1 | 0
GROSBEAK/ACSS/AW | 0.1369 | 0.1642 | 636 | 0.99 | 2 | 26/7 | 0.1564 | 19900 | 0.5809 | 16 | 832.2 | 0.1216 | 1 | 0
GROSBEAK/ACSS/TW | 0.1407 | 0.1689 | 636 | 0.908 | 2 | 20/7 | 0.1783 | 20700 | 0.5808 | 12 | 873.5 | 0.1216 | 1 | 0
PHEASANT/ACSS/TW | 0.0728 | 0.0867 | 1272 | 1.264 | 2 | 39/19 | 0.1806 | 34100 | 1.1256 | 17 | 1632 | 0.0921 | 1 | 0
PHEASANT/ACSS/AW | 0.0715 | 0.0873 | 1272 | 1.382 | 2 | 54/19 | 0.1535 | 32800 | 1.126 | 24 | 1568.1 | 0.0921 | 1 | 0
GRACKLE/ACSS | 0.0777 | 0.0951 | 1192.5 | 1.338 | 2 | 54/19 | 0.1486 | 32500 | 1.055 | 24 | 1533 | 0.0892 | 1 | 0
FLICKER/ACSS/AW | 0.1838 | 0.2207 | 477 | 0.846 | 2 | 24/7 | 0.141 | 12500 | 0.4232 | 15 | 588.8 | 0.094 | 1 | 0
CORNCRAKE/ACSS/AW | 0.0956 | 0.1141 | 954 | 1.165 | 2 | 20/7 | 0.7492 | 16200 | 0.801 | 13 | 1047.2 | 0.0971 | 1 | 0
PTARMIGAN/ACSS | 0.2277 | 0.2737 | 397.5 | 0.752 | 2 | 20/7 | 0.141 | 7090 | 0.3339 | 13 | 447.7 | 0.0627 | 1 | 0
CUCKOO/ACSS | 0.1141 | 0.1367 | 795 | 1.092 | 2 | 24/7 | 0.182 | 21700 | 0.7053 | 15 | 1022.7 | 0.1213 | 1 | 0
POWDER/ACSS/TW | 0.0464 | 0.0543 | 2153.8 | 1.602 | 2 | 64/19 | 0.1834 | 42100 | 1.829 | 22 | 2498 | 0.0961 | 1 | 0
FLAMINGO/ACSS | 0.1355 | 0.1625 | 666.6 | 1 | 2 | 24/7 | 0.1667 | 18200 | 0.5914 | 15 | 858 | 0.1111 | 1 | 0
FLAMINGO/ACSS/AW | 0.1322 | 0.1585 | 666.6 | 1 | 2 | 24/7 | 0.1667 | 17500 | 0.5914 | 15 | 822.9 | 0.1111 | 1 | 0
GANNET/ACSS | 0.1348 | 0.1617 | 666.6 | 1.014 | 2 | 26/7 | 0.1601 | 21700 | 0.6037 | 16 | 917 | 0.1245 | 1 | 0
FLICKER/ACSS | 0.1885 | 0.2264 | 477 | 0.846 | 2 | 24/7 | 0.141 | 13000 | 0.4232 | 15 | 615 | 0.094 | 1 | 0
LAPWING/ACSS/TW | 0.0602 | 0.0712 | 1590 | 1.358 | 2 | 36/7 | 0.2102 | 27900 | 1.3351 | 16 | 1790 | 0.1253 | 1 | 0
FLICKER/ACSS/TW | 0.1877 | 0.2255 | 477 | 0.776 | 2 | 18/7 | 0.1628 | 13000 | 0.4233 | 10 | 612.8 | 0.094 | 1 | 0
BALDPATE/ACSS | 0.0997 | 0.1196 | 900 | 1.212 | 2 | 30/7 | 0.1732 | 38700 | 0.8711 | 18 | 1410 | 0.1732 | 1 | 0
FRASER/ACSS/TW | 0.0969 | 0.1159 | 946.7 | 1.077 | 2 | 35/7 | 0.1645 | 21100 | 0.8168 | 16 | 1142 | 0.1154 | 1 | 0
PLOVER/ACSS/TW | 0.0652 | 0.0775 | 1431 | 1.337 | 2 | 37/19 | 0.1967 | 38400 | 1.2664 | 17 | 1834 | 0.0977 | 1 | 0
PLOVER/ACSS/AW | 0.0641 | 0.0781 | 1431 | 1.465 | 2 | 54/19 | 0.1628 | 36900 | 1.267 | 24 | 1764 | 0.0977 | 1 | 0
FINCH/ACSS/TW | 0.0826 | 0.0986 | 1113 | 1.185 | 2 | 38/19 | 0.1771 | 30400 | 0.9851 | 16 | 1429 | 0.0862 | 1 | 0
POTOMAC/ACSS/TW | 0.0613 | 0.0726 | 1557.4 | 1.345 | 2 | 36/7 | 0.208 | 27300 | 1.3079 | 16 | 1755 | 0.1241 | 1 | 0
BLUEJAY/ACSS/AW | 0.0826 | 0.099 | 1113 | 1.258 | 2 | 45/7 | 0.1573 | 18900 | 0.935 | 21 | 1222.2 | 0.1049 | 1 | 0
SNOWBIRD/ACSS/AW | 0.0892 | 0.1064 | 1033.5 | 1.203 | 2 | 42/7 | 0.1569 | 14800 | 0.8539 | 20 | 1093.8 | 0.0872 | 1 | 0
SNOWBIRD/ACSS/TW | 0.0899 | 0.1072 | 1033.5 | 1.089 | 2 | 30/7 | 0.1856 | 15400 | 0.8534 | 14 | 1115 | 0.0871 | 1 | 0
BLUEJAY/ACSS | 0.0837 | 0.1003 | 1113 | 1.258 | 2 | 45/7 | 0.1573 | 19500 | 0.935 | 21 | 1255 | 0.1049 | 1 | 0
MIRAMICHI/ACSS/TW | 0.0652 | 0.0773 | 1455.3 | 1.302 | 2 | 36/7 | 0.2011 | 25600 | 1.2222 | 16 | 1640 | 0.12 | 1 | 0
SQUAB/ACSS | 0.1483 | 0.178 | 605 | 0.966 | 2 | 26/7 | 0.1525 | 19700 | 0.5525 | 16 | 831.3 | 0.1186 | 1 | 0
SQUAB/ACSS/AW | 0.1438 | 0.1725 | 605 | 0.966 | 2 | 26/7 | 0.1525 | 19000 | 0.5525 | 16 | 791.3 | 0.1186 | 1 | 0
MERGANSER/ACSS | 0.0942 | 0.1125 | 954 | 1.248 | 2 | 30/7 | 0.1785 | 41100 | 0.9238 | 18 | 1493 | 0.1785 | 1 | 0
ST CROIX/ACSS/TW | 0.065 | 0.077 | 1467.8 | 1.292 | 2 | 33/7 | 0.2109 | 21600 | 1.2124 | 15 | 1585 | 0.1041 | 1 | 0
CANVASBACK/ACSS | 0.0942 | 0.1128 | 954 | 1.248 | 2 | 30/19 | 0.1783 | 41100 | 0.9199 | 18 | 1480.1 | 0.107 | 1 | 0
BLUEJAY/ACSS/TW | 0.0835 | 0.0996 | 1113 | 1.143 | 2 | 33/7 | 0.1836 | 19500 | 0.9347 | 15 | 1257 | 0.1049 | 1 | 0
STARLING/ACSS | 0.1258 | 0.1508 | 715.5 | 1.051 | 2 | 26/7 | 0.1659 | 23300 | 0.6535 | 16 | 985 | 0.129 | 1 | 0
STARLING/ACSS/AW | 0.122 | 0.1462 | 715.5 | 1.051 | 2 | 26/7 | 0.1659 | 22000 | 0.6535 | 16 | 936.4 | 0.129 | 1 | 0
STILT/ACSS | 0.1264 | 0.1516 | 715.5 | 1.044 | 2 | 24/7 | 0.1727 | 19500 | 0.6348 | 15 | 922 | 0.1151 | 1 | 0
STILT/ACSS/AW | 0.1234 | 0.1478 | 715.5 | 1.044 | 2 | 24/7 | 0.1727 | 18800 | 0.6348 | 15 | 883.1 | 0.1151 | 1 | 0
RUDDY/ACSS | 0.1023 | 0.1232 | 900 | 1.131 | 2 | 45/7 | 0.1414 | 15800 | 0.7555 | 21 | 1015 | 0.0943 | 1 | 0
MERRIMACK/ACSS/TW | 0.0651 | 0.0774 | 1433.6 | 1.34 | 2 | 39/19 | 0.1917 | 38400 | 1.2677 | 17 | 1840 | 0.0978 | 1 | 0
MYSTIC/ACSS/TW | 0.1349 | 0.1619 | 666.6 | 0.913 | 2 | 20/7 | 0.1826 | 18200 | 0.5914 | 12 | 856.3 | 0.1111 | 1 | 0
RUDDY/ACSS/AW | 0.101 | 0.1216 | 900 | 1.131 | 2 | 45/7 | 0.1414 | 15300 | 0.7555 | 21 | 987.6 | 0.0943 | 1 | 0
CARDINAL/ACSS/TW | 0.0952 | 0.1138 | 954 | 1.084 | 2 | 20/7 | 0.2184 | 26000 | 0.8464 | 12 | 1226 | 0.1329 | 1 | 0
SANTEE/ACSS/TW | 0.0396 | 0.0459 | 2627.3 | 1.762 | 2 | 64/19 | 0.2026 | 51300 | 2.2268 | 22 | 3048 | 0.1062 | 1 | 0
CONDOR/ACSS | 0.1141 | 0.1406 | 795 | 1.092 | 2 | 54/7 | 0.1213 | 21700 | 0.7053 | 24 | 1024 | 0.1213 | 1 | 0
SAPSUCKER/ACSS | 0.1626 | 0.1952 | 556.5 | 0.901 | 2 | 22/7 | 0.159 | 12600 | 0.4797 | 14 | 669 | 0.0883 | 1 | 0
LAPWING/ACSS | 0.0605 | 0.0718 | 1590 | 1.504 | 2 | 45/7 | 0.188 | 27900 | 1.335 | 21 | 1792 | 0.1253 | 1 | 0
SNOWBIRD/ACSS | 0.0901 | 0.1074 | 1033.5 | 1.203 | 2 | 42/7 | 0.1569 | 15400 | 0.8539 | 20 | 1115.4 | 0.0872 | 1 | 0
SCHUYKILL/ACSS/TW | 0.0581 | 0.0685 | 1657.4 | 1.386 | 2 | 36/7 | 0.2146 | 29100 | 1.392 | 16 | 1868 | 0.128 | 1 | 0
MOCKINGBIRD/ACSS | 0.0498 | 0.0581 | 2034.5 | 1.681 | 2 | 72/7 | 0.1681 | 27200 | 1.667 | 27 | 2159.6 | 0.1121 | 1 | 0
SCISSORTAIL/ACSS/TW | 0.0741 | 0.088 | 1272 | 1.203 | 2 | 30/7 | 0.2059 | 18700 | 1.0505 | 14 | 1372 | 0.0967 | 1 | 0
SCOTER/ACSS | 0.1401 | 0.1681 | 636 | 1.019 | 2 | 30/7 | 0.1456 | 27400 | 0.616 | 18 | 995.1 | 0.1456 | 1 | 0
SCOTER/ACSS/AW | 0.1341 | 0.1608 | 636 | 1.019 | 2 | 30/7 | 0.1456 | 25100 | 0.616 | 18 | 934.8 | 0.1456 | 1 | 0
MOHAWK/ACSS/TW | 0.157 | 0.1884 | 571.7 | 0.846 | 2 | 18/7 | 0.1782 | 15600 | 0.5074 | 10 | 734.7 | 0.103 | 1 | 0
MOCKINGBIRD/ACSS/AW | 0.0494 | 0.0577 | 2034.5 | 1.681 | 2 | 72/7 | 0.1681 | 26500 | 1.667 | 27 | 2123.9 | 0.1121 | 1 | 0
CANVASBACK/ACSS/AW | 0.0903 | 0.108 | 954 | 1.248 | 2 | 30/19 | 0.1783 | 39400 | 0.9199 | 18 | 1391.6 | 0.107 | 1 | 0
MAUMEE/ACSS/TW | 0.1174 | 0.1407 | 768.2 | 0.977 | 2 | 20/7 | 0.196 | 21000 | 0.6819 | 12 | 987.8 | 0.1195 | 1 | 0
CARDINAL/ACSS | 0.0956 | 0.1176 | 954 | 1.196 | 2 | 54/7 | 0.1329 | 26000 | 0.8463 | 24 | 1229 | 0.1329 | 1 | 0
BUNTING/ACSS/AW | 0.0775 | 0.0927 | 1192.5 | 1.302 | 2 | 45/7 | 0.1628 | 20300 | 1.001 | 21 | 1309.1 | 0.1085 | 1 | 0
TOWHEE/ACSS | 0.0964 | 0.1152 | 954 | 1.175 | 2 | 48/7 | 0.141 | 19700 | 0.8157 | 22 | 1122.8 | 0.1097 | 1 | 0
TOWHEE/ACSS/AW | 0.0948 | 0.1132 | 954 | 1.175 | 2 | 48/7 | 0.141 | 19000 | 0.8157 | 22 | 1088.6 | 0.1097 | 1 | 0
CALUMET/ACSS/TW | 0.1581 | 0.1898 | 565.3 | 0.858 | 2 | 18/7 | 0.1772 | 18400 | 0.5165 | 10 | 714.8 | 0.1147 | 1 | 0
TRUCKEE/ACSS/TW | 0.0691 | 0.0819 | 1372.5 | 1.248 | 2 | 30/7 | 0.2139 | 20200 | 1.1334 | 14 | 1481 | 0.1004 | 1 | 0
BRANT/ACSS | 0.2759 | 0.2714 | 397.5 | 0.772 | 2 | 24/7 | 0.1287 | 11100 | 0.3525 | 15 | 512 | 0.0858 | 1 | 0
BRANT/ACSS/AW | 0.2202 | 0.2646 | 397.5 | 0.772 | 2 | 24/7 | 0.1287 | 10400 | 0.3525 | 15 | 490.5 | 0.0858 | 1 | 0
SUWANNEE/ACSS/TW | 0.0941 | 0.1127 | 959.6 | 1.108 | 2 | 22/7 | 0.2088 | 30700 | 0.8762 | 13 | 1318 | 0.1493 | 1 | 0
BUNTING/ACSS/TW | 0.0783 | 0.0932 | 1192.5 | 1.181 | 2 | 33/7 | 0.1901 | 20900 | 1.0013 | 15 | 1343 | 0.1085 | 1 | 0
THRASHER/ACSS | 0.0447 | 0.0519 | 2312 | 1.802 | 2 | 76/19 | 0.1744 | 35600 | 1.9144 | 28 | 2523.3 | 0.0814 | 1 | 0
BUNTING/ACSS | 0.0785 | 0.0939 | 1192.5 | 1.302 | 2 | 45/7 | 0.1628 | 20900 | 1.001 | 21 | 1344 | 0.1085 | 1 | 0
WOODCOCK/ACSS/AW | 0.2626 | 0.3156 | 336.4 | 0.701 | 2 | 22/7 | 0.1237 | 7210 | 0.2903 | 14 | 391.5 | 0.0687 | 1 | 0
WOODCOCK/ACSS | 0.2677 | 0.3218 | 336.4 | 0.701 | 2 | 22/7 | 0.1237 | 7610 | 0.2903 | 14 | 404.9 | 0.0687 | 1 | 0
WABASH/ACSS/TW | 0.1141 | 0.1411 | 762.8 | 0.99 | 2 | 20/7 | 0.1953 | 24900 | 0.6966 | 12 | 1047 | 0.1331 | 1 | 0
WOOD DUCK/ACSS/AW | 0.1408 | 0.1689 | 605 | 0.994 | 2 | 30/7 | 0.142 | 24400 | 0.586 | 18 | 889.2 | 0.142 | 1 | 0
WOOD DUCK/ACSS | 0.1471 | 0.1766 | 605 | 0.994 | 2 | 30/7 | 0.142 | 26100 | 0.586 | 18 | 946.5 | 0.142 | 1 | 0
YUKON/ACSS/TW | 0.0749 | 0.0893 | 1233.6 | 1.245 | 2 | 38/19 | 0.1802 | 33200 | 1.0925 | 16 | 1586 | 0.091 | 1 | 0
TERN/ACSS | 0.1153 | 0.139 | 795 | 1.063 | 2 | 45/7 | 0.1329 | 14200 | 0.6676 | 21 | 896 | 0.0886 | 1 | 0
CANARY/ACSS/AW | 0.0987 | 0.1214 | 900 | 1.141 | 2 | 54/7 | 0.1291 | 23200 | 0.7985 | 24 | 1110.6 | 0.1291 | 1 | 0
TAILORBIRD/ACSS | 0.1901 | 0.2284 | 477 | 0.824 | 2 | 20/7 | 0.1544 | 8490 | 0.4004 | 13 | 536.7 | 0.0686 | 1 | 0
TAILORBIRD/ACSS/AW | 0.1876 | 0.2253 | 477 | 0.824 | 2 | 20/7 | 0.1544 | 8100 | 0.4004 | 13 | 523.3 | 0.0686 | 1 | 0
CANARY/ACSS | 0.1012 | 0.1245 | 900 | 1.141 | 2 | 54/7 | 0.1291 | 24500 | 0.7985 | 24 | 1159 | 0.1291 | 1 | 0
TEAL/ACSS | 0.1472 | 0.1767 | 605 | 0.994 | 2 | 30/19 | 0.142 | 26600 | 0.5835 | 18 | 940 | 0.0852 | 1 | 0
TEAL/ACSS/AW | 0.1411 | 0.1692 | 605 | 0.994 | 2 | 30/19 | 0.142 | 25000 | 0.5835 | 18 | 882.6 | 0.0852 | 1 | 0
BOBOLINK/ACSS/TW | 0.0662 | 0.0785 | 1431 | 1.291 | 2 | 36/7 | 0.1994 | 25100 | 1.2017 | 16 | 1611 | 0.1189 | 1 | 0
MARTIN/ACSS/AW | 0.0676 | 0.0824 | 1351.5 | 1.424 | 2 | 54/19 | 0.1582 | 34900 | 1.196 | 24 | 1665.4 | 0.0949 | 1 | 0
THRASHER/ACSS/AW | 0.0443 | 0.0514 | 2312 | 1.802 | 2 | 76/19 | 0.1744 | 34100 | 1.9144 | 28 | 2472.1 | 0.0814 | 1 | 0
TERN/ACSS/AW | 0.1138 | 0.1372 | 795 | 1.063 | 2 | 45/7 | 0.1329 | 13500 | 0.6676 | 21 | 872.4 | 0.0886 | 1 | 0
TERN/ACSS/TW | 0.1147 | 0.1373 | 795 | 0.96 | 2 | 17/7 | 0.2163 | 14200 | 0.6675 | 9 | 892 | 0.0886 | 1 | 0
MARTIN/ACSS | 0.0692 | 0.0844 | 1351.5 | 1.424 | 2 | 54/19 | 0.1582 | 36200 | 1.196 | 24 | 1737 | 0.0949 | 1 | 0
THAMES/ACSS/TW | 0.0696 | 0.0828 | 1334.6 | 1.29 | 2 | 39/19 | 0.185 | 35800 | 1.1809 | 17 | 1713 | 0.0944 | 1 | 0
BOBOLINK/ACSS | 0.0664 | 0.0791 | 1431 | 1.427 | 2 | 45/7 | 0.1783 | 25100 | 1.201 | 21 | 1613 | 0.1189 | 1 | 0
BOBOLINK/ACSS/AW | 0.0656 | 0.0781 | 1431 | 1.427 | 2 | 45/7 | 0.1783 | 24300 | 1.201 | 21 | 1570.5 | 0.1189 | 1 | 0
CARDINAL/ACSS/AW | 0.0934 | 0.1147 | 954 | 1.196 | 2 | 54/7 | 0.1329 | 24600 | 0.8463 | 24 | 1176.9 | 0.1329 | 1 | 0
MARTIN/ACSS/TW | 0.0688 | 0.0819 | 1351.5 | 1.3 | 2 | 39/19 | 0.1862 | 36200 | 1.1959 | 17 | 1734 | 0.0949 | 1 | 0
SAPSUCKER/ACSS/AW | 0.1551 | 0.1915 | 556.5 | 0.901 | 2 | 22/7 | 0.159 | 11900 | 0.4797 | 14 | 646.9 | 0.0883 | 1 | 0
MACKENZIE/ACSS/TW | 0.0694 | 0.0823 | 1359.7 | 1.259 | 2 | 36/7 | 0.1943 | 23900 | 1.1418 | 16 | 1530 | 0.1159 | 1 | 0
CHUKAR/ACSS | 0.0547 | 0.0645 | 1781 | 1.602 | 2 | 84/19 | 0.1456 | 35300 | 1.513 | 30 | 2075 | 0.0874 | 1 | 0
LARK/ACSS | 0.2233 | 0.2681 | 397.5 | 0.806 | 2 | 30/7 | 0.1151 | 17500 | 0.385 | 18 | 623 | 0.1151 | 1 | 0
LARK/ACSS/AW | 0.2135 | 0.2564 | 397.5 | 0.806 | 2 | 30/7 | 0.1151 | 16700 | 0.385 | 18 | 584.2 | 0.1151 | 1 | 0
OXBIRD/ACSS/TW | 0.0786 | 0.0935 | 1192.5 | 1.167 | 2 | 30/7 | 0.1994 | 17500 | 0.9848 | 14 | 1286 | 0.0936 | 1 | 0
OSWEGO/ACSS/TW | 0.1347 | 0.1617 | 664.8 | 0.927 | 2 | 20/7 | 0.1823 | 21700 | 0.6072 | 12 | 913.4 | 0.1244 | 1 | 0
CHUKAR/ACSS/TW | 0.0542 | 0.0639 | 1780 | 1.445 | 2 | 37/19 | 0.2193 | 35300 | 1.512 | 17 | 2061 | 0.0874 | 1 | 0
OSTRICH/ACSS | 0.2976 | 0.3575 | 300 | 0.68 | 2 | 26/7 | 0.1074 | 9970 | 0.2744 | 16 | 413 | 0.0835 | 1 | 0
LAPWING/ACSS/AW | 0.0597 | 0.0709 | 1590 | 1.504 | 2 | 45/7 | 0.188 | 27000 | 1.335 | 21 | 1745.7 | 0.1253 | 1 | 0
LINNET/ACSS | 0.2655 | 0.319 | 336.4 | 0.72 | 2 | 26/7 | 0.1137 | 11200 | 0.3072 | 16 | 463 | 0.0884 | 1 | 0
NELSON/ACSS/TW | 0.0745 | 0.0887 | 1257.1 | 1.213 | 2 | 35/7 | 0.1895 | 22100 | 1.0557 | 16 | 1417 | 0.1115 | 1 | 0
BLUEBIRD/ACSS | 0.0466 | 0.0544 | 2156 | 1.762 | 2 | 84/19 | 0.1602 | 42100 | 1.8309 | 30 | 2511 | 0.0961 | 1 | 0
MACAW/ACSS | 0.1157 | 0.1385 | 795 | 1.055 | 2 | 42/7 | 0.1376 | 11800 | 0.6567 | 20 | 857.6 | 0.0764 | 1 | 0
MACAW/ACSS/AW | 0.1146 | 0.1371 | 795 | 1.055 | 2 | 42/7 | 0.1376 | 11400 | 0.6567 | 20 | 841.1 | 0.0764 | 1 | 0
BLUEBIRD/ACSS/AW | 0.046 | 0.0537 | 2156 | 1.762 | 2 | 84/19 | 0.1602 | 40700 | 1.8309 | 30 | 2436.5 | 0.0961 | 1 | 0
OSTRICH/ACSS/AW | 0.2883 | 0.3464 | 300 | 0.68 | 2 | 26/7 | 0.1074 | 9390 | 0.2744 | 16 | 392.5 | 0.0835 | 1 | 0
PARROT/ACSS/AW | 0.0611 | 0.0742 | 1510.5 | 1.505 | 2 | 54/19 | 0.1672 | 38900 | 1.336 | 24 | 1860.3 | 0.1003 | 1 | 0
JOREE/ACSS | 0.0419 | 0.0484 | 2515 | 1.88 | 2 | 76/19 | 0.1819 | 38700 | 2.0826 | 28 | 2745 | 0.0849 | 1 | 0
JOREE/ACSS/AW | 0.0415 | 0.048 | 2515 | 1.88 | 2 | 76/19 | 0.1819 | 37100 | 2.0826 | 28 | 2689.3 | 0.0849 | 1 | 0
JUNCO/ACSS | 0.322 | 0.3991 | 266.8 | 0.66 | 2 | 30/7 | 0.0943 | 11700 | 0.2095 | 18 | 416.8 | 0.0943 | 1 | 0
JUNCO/ACSS/AW | 0.3176 | 0.3816 | 266.8 | 0.66 | 2 | 30/7 | 0.0943 | 11200 | 0.2095 | 18 | 391.5 | 0.0943 | 1 | 0
PARTRIDGE/ACSS/AW | 0.324 | 0.3894 | 266.8 | 0.642 | 2 | 26/7 | 0.1013 | 8360 | 0.2436 | 16 | 349.2 | 0.0788 | 1 | 0
PARTRIDGE/ACSS | 0.3343 | 0.4019 | 266.8 | 0.642 | 2 | 26/7 | 0.1013 | 8880 | 0.2436 | 16 | 366.9 | 0.0788 | 1 | 0
CHUKAR/ACSS/AW | 0.054 | 0.0635 | 1781 | 1.602 | 2 | 84/19 | 0.1456 | 33600 | 1.513 | 30 | 2013 | 0.0874 | 1 | 0
KETTLE/ACSS/TW | 0.0964 | 0.1152 | 957.2 | 1.06 | 2 | 32/7 | 0.173 | 16800 | 0.8038 | 14 | 1079 | 0.0973 | 1 | 0
LINNET/ACSS/AW | 0.2572 | 0.309 | 336.4 | 0.72 | 2 | 26/7 | 0.1137 | 10500 | 0.3072 | 16 | 439.8 | 0.0884 | 1 | 0
PARROT/ACSS | 0.0624 | 0.0759 | 1510.5 | 1.505 | 2 | 54/19 | 0.1672 | 40500 | 1.336 | 24 | 1940 | 0.1003 | 1 | 0
KIWI/ACSS | 0.0473 | 0.0551 | 2167 | 1.735 | 2 | 72/7 | 0.1735 | 29000 | 1.7758 | 27 | 2300.6 | 0.1157 | 1 | 0
KIWI/ACSS/AW | 0.047 | 0.0547 | 2167 | 1.735 | 2 | 72/7 | 0.1735 | 28200 | 1.7758 | 27 | 2262.5 | 0.1157 | 1 | 0
PARAKEET/ACSS/TW | 0.1612 | 0.1935 | 556.5 | 0.835 | 2 | 18/7 | 0.1758 | 15200 | 0.4937 | 10 | 714.9 | 0.1015 | 1 | 0
PARAKEET/ACSS/AW | 0.1579 | 0.1894 | 556.5 | 0.914 | 2 | 24/7 | 0.1523 | 14600 | 0.4938 | 15 | 686.8 | 0.1015 | 1 | 0
PARAKEET/ACSS | 0.1618 | 0.1943 | 556.5 | 0.914 | 2 | 24/7 | 0.1523 | 15200 | 0.4938 | 15 | 717 | 0.1015 | 1 | 0
COLUMBIA/ACSS/TW | 0.094 | 0.1124 | 966.2 | 1.092 | 2 | 21/7 | 0.2145 | 26400 | 0.8573 | 13 | 1241 | 0.1338 | 1 | 0
ROADRUNNER/ACSS | 0.049 | 0.0573 | 2057 | 1.7 | 2 | 76/19 | 0.1645 | 31700 | 1.7032 | 28 | 2245.1 | 0.0768 | 1 | 0
REDWING/ACSS | 0.1248 | 0.1497 | 715.5 | 1.081 | 2 | 30/19 | 0.1544 | 30800 | 0.6901 | 18 | 1111 | 0.0926 | 1 | 0
REDWING/ACSS/AW | 0.1196 | 0.1434 | 715.5 | 1.081 | 2 | 30/19 | 0.1544 | 29500 | 0.6901 | 18 | 1043.1 | 0.0926 | 1 | 0
ORIOLE/ACSS/AW | 0.2521 | 0.3028 | 336.4 | 0.741 | 2 | 30/7 | 0.1059 | 14200 | 0.3259 | 18 | 494.6 | 0.1059 | 1 | 0
CATAWBA/ACSS/TW | 0.0741 | 0.088 | 1272 | 1.203 | 2 | 30/7 | 0.2059 | 18700 | 1.0505 | 14 | 1372 | 0.0967 | 1 | 0
CHEYENNE/ACSS/TW | 0.0801 | 0.0954 | 1168.1 | 1.155 | 2 | 30/7 | 0.1973 | 17200 | 0.9646 | 14 | 1260 | 0.0926 | 1 | 0
REDBIRD/ACSS/AW | 0.0934 | 0.1116 | 954 | 1.196 | 2 | 24/7 | 0.7495 | 24600 | 0.8466 | 15 | 1177.4 | 0.1329 | 1 | 0
RIO GRANDE/ACSS/TW | 0.0612 | 0.0726 | 1533.3 | 1.382 | 2 | 39/19 | 0.1983 | 41200 | 1.3571 | 17 | 1968 | 0.1012 | 1 | 0
ORIOLE/ACSS | 0.2637 | 0.3167 | 336.4 | 0.741 | 2 | 30/7 | 0.1059 | 14800 | 0.3259 | 18 | 527 | 0.1059 | 1 | 0
ROADRUNNER/ACSS/AW | 0.0486 | 0.0568 | 2057 | 1.7 | 2 | 76/19 | 0.1645 | 30300 | 1.7032 | 28 | 2199.5 | 0.0768 | 1 | 0
ROOK/ACSS | 0.1419 | 0.1702 | 636 | 0.977 | 2 | 24/7 | 0.1628 | 17400 | 0.5643 | 15 | 819 | 0.1085 | 1 | 0
ROOK/ACSS/AW | 0.1384 | 0.166 | 636 | 0.977 | 2 | 24/7 | 0.1628 | 16700 | 0.5643 | 15 | 784.8 | 0.1085 | 1 | 0
ROOK/ACSS/TW | 0.1413 | 0.1696 | 636 | 0.89 | 2 | 19/7 | 0.183 | 17300 | 0.5643 | 11 | 816 | 0.1085 | 1 | 0
NUTHATCH/ACSS/AW | 0.0625 | 0.0743 | 1510.5 | 1.465 | 2 | 45/7 | 0.1832 | 25700 | 1.268 | 21 | 1657.6 | 0.1221 | 1 | 0
NUTHATCH/ACSS | 0.0633 | 0.0752 | 1510.5 | 1.465 | 2 | 45/7 | 0.1832 | 26500 | 1.268 | 21 | 1703 | 0.1221 | 1 | 0
BLUEBIRD/ACSS/TW | 0.0464 | 0.0543 | 2156 | 1.608 | 2 | 64/19 | 0.1836 | 42100 | 1.8321 | 22 | 2512 | 0.0961 | 1 | 0
ORTOLAN/ACSS/AW | 0.0886 | 0.1063 | 1033.5 | 1.212 | 2 | 45/7 | 0.1515 | 17600 | 0.8673 | 21 | 1133.7 | 0.101 | 1 | 0
MALLARD/ACSS/AW | 0.1079 | 0.1292 | 795 | 1.14 | 2 | 30/19 | 0.1628 | 32900 | 0.7668 | 18 | 1160.1 | 0.0977 | 1 | 0
REDBIRD/ACSS | 0.0956 | 0.1144 | 954 | 1.196 | 2 | 24/7 | 0.7495 | 26000 | 0.8466 | 15 | 1227.5 | 0.1329 | 1 | 0
ORTOLAN/ACSS | 0.0897 | 0.1077 | 1033.5 | 1.212 | 2 | 45/7 | 0.1515 | 18100 | 0.8673 | 21 | 1164 | 0.101 | 1 | 0
MALLARD/ACSS | 0.1125 | 0.1349 | 795 | 1.14 | 2 | 30/19 | 0.1628 | 34300 | 0.7668 | 18 | 1235 | 0.0977 | 1 | 0
ORTOLAN/ACSS/TW | 0.0896 | 0.1069 | 1033.5 | 1.102 | 2 | 32/7 | 0.1797 | 18100 | 0.8673 | 14 | 1165 | 0.101 | 1 | 0
COCKSCOMB | 0.106 | 0.126 | 900 | 1.092 | 4 | 37/0 | 0.156 | 15400 | 0.7072 | 18 | 845.2 | 9999 | 1 | 0
ARBUTUS | 0.12 | 0.142 | 795 | 1.026 | 4 | 37/0 | 0.1466 | 13900 | 0.6245 | 18 | 746.4 | 9999 | 1 | 0
ANEMONE | 0.109 | 0.13 | 874.5 | 1.077 | 4 | 37/0 | 0.1538 | 15000 | 0.6874 | 18 | 821 | 9999 | 1 | 0
COLUMBINE | 0.0731 | 0.0861 | 1351.5 | 1.34 | 4 | 61/0 | 0.1489 | 23400 | 1.062 | 24 | 1269 | 9999 | 1 | 0
COSMOS/T2 | 0.1007 | 0.1195 | 954 | 1.298 | 4 | 19/0 | 0.1584 | 16700 | 0.7492 | 12 | 894.6 | 9999 | 1 | 0
ASTER/T2 | 0.3508 | 0.4199 | 266.2 | 0.678 | 4 | 7/0 | 0.1379 | 5020 | 0.209 | 6 | 249.8 | 9999 | 1 | 0
CARNATION | 0.0695 | 0.0817 | 1431 | 1.379 | 4 | 61/0 | 0.1532 | 24300 | 1.124 | 24 | 1344 | 9999 | 1 | 0
BLUEBONNET | 0.0357 | 0.0402 | 3500 | 2.158 | 4 | 127/0 | 0.166 | 58700 | 2.749 | 36 | 3350 | 9999 | 1 | 0
CROCUS | 0.109 | 0.13 | 874.5 | 1.078 | 4 | 61/0 | 0.1198 | 15800 | 0.6876 | 24 | 821 | 9999 | 1 | 0
DAFFODIL | 0.267 | 0.32 | 350 | 0.679 | 4 | 19/0 | 0.1357 | 6390 | 0.2748 | 12 | 328.4 | 9999 | 1 | 0
DAHLIA | 0.169 | 0.202 | 556.5 | 0.855 | 4 | 19/0 | 0.1711 | 9750 | 0.4369 | 12 | 522.1 | 9999 | 1 | 0
CHAFER | 0.2654 | 0.2704 | 407.53 | 0.745 | 4 | 19/0 | 0.1488 | 7479 | 0.3314 | 12 | 395.5 | 9999 | 1 | 0
CICADA | 0.0904 | 0.0449 | 1187.27 | 1.281 | 4 | 37/0 | 0.1831 | 20320 | 0.9731 | 18 | 1165.4 | 9999 | 1 | 0
ASTER | 0.7 | 0.838 | 133.1 | 0.414 | 4 | 7/0 | 0.1379 | 2510 | 0.1045 | 6 | 124.9 | 9999 | 1 | 0
COREOPSIS | 0.0634 | 0.0743 | 1590 | 1.454 | 4 | 61/0 | 0.1615 | 27000 | 1.25 | 24 | 1493 | 9999 | 1 | 0
BUTTERFLY | 0.1756 | 0.1867 | 614.55 | 0.915 | 4 | 19/0 | 0.1831 | 10901 | 0.4997 | 12 | 596.3 | 9999 | 1 | 0
CENTIPEDE | 0.1362 | 0.1365 | 787.43 | 1.043 | 4 | 37/0 | 0.1488 | 13920 | 0.6453 | 18 | 772.6 | 9999 | 1 | 0
IRIS/T2 | 0.7022 | 0.8411 | 132.7 | 0.478 | 4 | 7/0 | 0.0974 | 2700 | 0.1042 | 6 | 124.5 | 9999 | 1 | 0
DAHLIA/T2 | 0.0872 | 0.1032 | 1113 | 1.401 | 4 | 19/0 | 0.1711 | 19500 | 0.8742 | 12 | 1043.8 | 9999 | 1 | 0
CANNA | 0.235 | 0.282 | 397.5 | 0.723 | 4 | 19/0 | 0.1447 | 7110 | 0.3124 | 12 | 373.4 | 9999 | 1 | 0
CANNA/T2 | 0.1197 | 0.1425 | 795 | 1.185 | 4 | 19/0 | 0.1447 | 14200 | 0.6244 | 12 | 746.5 | 9999 | 1 | 0
COSMOS | 0.197 | 0.235 | 477 | 0.793 | 4 | 19/0 | 0.1584 | 8360 | 0.3744 | 12 | 447.5 | 9999 | 1 | 0
COWSLIP | 0.0525 | 0.0609 | 2000 | 1.631 | 4 | 91/0 | 0.1482 | 34200 | 1.57 | 30 | 1876 | 9999 | 1 | 0
CAMELLIA | 0.0964 | 0.114 | 1000 | 1.152 | 4 | 61/0 | 0.128 | 17700 | 0.7849 | 24 | 938.2 | 9999 | 1 | 0
CATTAIL | 0.127 | 0.151 | 750 | 0.998 | 4 | 61/0 | 0.1109 | 13500 | 0.5892 | 24 | 704.2 | 9999 | 1 | 0
BLUEBELL | 0.0933 | 0.111 | 1033.5 | 1.17 | 4 | 37/0 | 0.1672 | 17700 | 0.8124 | 18 | 970.9 | 9999 | 1 | 0
COCKROACH | 0.2123 | 0.2301 | 505.81 | 0.83 | 4 | 19/0 | 0.1661 | 9120 | 0.4112 | 12 | 490.7 | 9999 | 1 | 0
TRITON | 0.1388 | 0.1405 | 789.41 | 1.035 | 4 | 37/0 | 0.1476 | 14140 | 0.6335 | 18 | 759.3 | 9999 | 1 | 0
FLY | 0.8827 | 0.9463 | 124.33 | 0.402 | 4 | 7/0 | 0.1339 | 2320 | 0.0987 | 7 | 117 | 9999 | 1 | 0
ROSE | 2.232 | 2.674 | 41.74 | 0.232 | 4 | 7/0 | 0.0772 | 881 | 0.0328 | 7 | 39.2 | 9999 | 1 | 0
ROSE/T2 | 1.1153 | 1.2257 | 83.5 | 0.38 | 4 | 7/0 | 0.0772 | 1762 | 0.0656 | 6 | 78.3 | 9999 | 1 | 0
SATURN | 0.2163 | 0.2173 | 505.22 | 0.827 | 4 | 37/0 | 0.1181 | 9397.013 | 0.4053 | 37 | 484.4904 | 9999 | 1 | 0
SCORPION | 0.1073 | 0.0972 | 1000.97 | 1.176 | 4 | 37/0 | 0.1681 | 17301 | 0.8203 | 18 | 982.3 | 9999 | 1 | 0
SNAPDRAGON | 0.106 | 0.126 | 900 | 1.094 | 4 | 61/0 | 0.1215 | 15900 | 0.7072 | 24 | 845.3 | 9999 | 1 | 0
SNEEZEWORT | 0.373 | 0.447 | 250 | 0.567 | 4 | 7/0 | 0.189 | 4520 | 0.1964 | 6 | 234.7 | 9999 | 1 | 0
SYRINGA | 0.197 | 0.235 | 477 | 0.795 | 4 | 37/0 | 0.1135 | 8690 | 0.3743 | 18 | 447.4 | 9999 | 1 | 0
VIRGO | 0.0393 | 0.0439 | 2782.66 | 1.949 | 4 | 91/0 | 0.1772 | 46535.4472 | 2.2429 | 91 | 2694.5997 | 9999 | 1 | 0
DAISY | 0.35 | 0.419 | 266.8 | 0.586 | 4 | 7/0 | 0.1953 | 4830 | 0.2097 | 6 | 250.6 | 9999 | 1 | 0
GOLDENROD | 0.101 | 0.119 | 954 | 1.126 | 4 | 61/0 | 0.1251 | 16900 | 0.7498 | 24 | 896.1 | 9999 | 1 | 0
TRILLIUM | 0.0392 | 0.0445 | 3000 | 1.998 | 4 | 127/0 | 0.1537 | 50300 | 2.356 | 36 | 2844 | 9999 | 1 | 0
TULIP/T2 | 0.1406 | 0.1676 | 672.8 | 1.09 | 4 | 19/0 | 0.1331 | 12300 | 0.5284 | 12 | 631.6 | 9999 | 1 | 0
URANUS | 0.1125 | 0.1144 | 972.95 | 1.154 | 4 | 61/0 | 0.128 | 16905.6311 | 0.7843 | 61 | 940.758 | 9999 | 1 | 0
VALERIAN | 0.373 | 0.447 | 250 | 0.573 | 4 | 19/0 | 0.1147 | 4660 | 0.1963 | 12 | 234.6 | 9999 | 1 | 0
VENUS | 0.0843 | 0.0869 | 1300.55 | 1.331 | 4 | 61/0 | 0.1476 | 22099 | 1.0442 | 24 | 1249.9 | 9999 | 1 | 0
VENUS | 0.0843 | 0.0869 | 1300.55 | 1.331 | 4 | 61/0 | 0.1476 | 22098.7172 | 1.0442 | 61 | 1249.8642 | 9999 | 1 | 0
VERBENA | 0.135 | 0.161 | 700 | 0.962 | 4 | 37/0 | 0.1375 | 12500 | 0.5494 | 18 | 656.6 | 9999 | 1 | 0
VIOLET | 0.132 | 0.158 | 715.5 | 0.974 | 4 | 37/0 | 0.1391 | 12800 | 0.5622 | 18 | 672 | 9999 | 1 | 0
TAURUS | 0.1685 | 0.1706 | 653.24 | 0.937 | 4 | 19/0 | 0.187 | 11442.7742 | 0.5219 | 19 | 622.2442 | 9999 | 1 | 0
HYACINTH | 0.188 | 0.225 | 500 | 0.813 | 4 | 37/0 | 0.1162 | 9110 | 0.3924 | 18 | 469 | 9999 | 1 | 0
LARKSPUR | 0.0933 | 0.111 | 1033.5 | 1.172 | 4 | 61/0 | 0.1302 | 18300 | 0.8122 | 24 | 970.6 | 9999 | 1 | 0
LAUREL | 0.35 | 0.419 | 266.8 | 0.593 | 4 | 19/0 | 0.1185 | 4970 | 0.2095 | 12 | 250.4 | 9999 | 1 | 0
LEO | 1.6377 | 1.6415 | 66.9 | 0.295 | 4 | 7/0 | 0.0984 | 1292.6513 | 0.0533 | 7 | 63.3668 | 9999 | 1 | 0
LIBRA | 1.1383 | 1.1394 | 96.31 | 0.354 | 4 | 7/0 | 0.1181 | 1778.2386 | 0.0767 | 7 | 90.716 | 9999 | 1 | 0
JUPITER | 2.025 | 2.0277 | 54.27 | 0.266 | 4 | 7/0 | 0.0886 | 1070.0905 | 0.0431 | 7 | 51.0025 | 9999 | 1 | 0
JEWELWEED | 0.0525 | 0.0609 | 2000 | 1.63 | 4 | 61/0 | 0.1811 | 34200 | 1.571 | 24 | 1876 | 9999 | 1 | 0
JESSAMINE | 0.0585 | 0.0683 | 1750 | 1.525 | 4 | 61/0 | 0.1694 | 29700 | 1.375 | 24 | 1643 | 9999 | 1 | 0
LILAC | 0.12 | 0.142 | 795 | 1.028 | 4 | 61/0 | 0.1142 | 14300 | 0.6248 | 24 | 746.7 | 9999 | 1 | 0
GEMINI | 3.3619 | 3.3634 | 32.76 | 0.207 | 4 | 7/0 | 0.0689 | 676.6749 | 0.0261 | 7 | 30.9778 | 9999 | 1 | 0
LILY/T2 | 0.8846 | 1.0595 | 105.2 | 0.426 | 4 | 7/0 | 0.0867 | 2180 | 0.0827 | 6 | 98.7 | 9999 | 1 | 0
GLADIOLUS | 0.0663 | 0.0778 | 1511 | 1.417 | 4 | 61/0 | 0.1574 | 25600 | 1.187 | 24 | 1419 | 9999 | 1 | 0
HORNET | 0.3598 | 0.3621 | 300.76 | 0.64 | 4 | 19/0 | 0.128 | 5681 | 0.2445 | 12 | 291.6 | 9999 | 1 | 0
HAWTHORN | 0.0819 | 0.0968 | 1192.5 | 1.258 | 4 | 61/0 | 0.1398 | 21100 | 0.9363 | 24 | 1119 | 9999 | 1 | 0
HAWKWEED | 0.0963 | 0.114 | 1000 | 1.151 | 4 | 37/0 | 0.1644 | 17200 | 0.7854 | 18 | 938.7 | 9999 | 1 | 0
GRUB | 1.1363 | 1.1394 | 96.51 | 0.354 | 4 | 7/0 | 0.1181 | 1850 | 0.0766 | 7 | 90.6 | 9999 | 1 | 0
LUPINE | 0.0446 | 0.0512 | 2500 | 1.823 | 4 | 91/0 | 0.1657 | 41800 | 1.962 | 30 | 2368 | 9999 | 1 | 0
MAGNOLIA | 0.101 | 0.12 | 954 | 1.124 | 4 | 37/0 | 0.1606 | 16400 | 0.7495 | 18 | 895.8 | 9999 | 1 | 0
MARIGOLD | 0.0872 | 0.103 | 1113 | 1.216 | 4 | 61/0 | 0.1351 | 19700 | 0.8744 | 24 | 1045 | 9999 | 1 | 0
GOLDENTUFT | 0.208 | 0.249 | 450 | 0.769 | 4 | 19/0 | 0.1539 | 7890 | 0.3534 | 12 | 422.4 | 9999 | 1 | 0
TULIP | 0.278 | 0.332 | 336.4 | 0.666 | 4 | 19/0 | 0.1331 | 6150 | 0.2644 | 12 | 316 | 9999 | 1 | 0
IRIS | 1.402 | 1.68 | 66.36 | 0.292 | 4 | 7/0 | 0.0974 | 1350 | 0.0522 | 6 | 62.3 | 9999 | 1 | 0
PETUNIA | 0.127 | 0.151 | 750 | 0.997 | 4 | 37/0 | 0.1424 | 13100 | 0.5892 | 18 | 704.3 | 9999 | 1 | 0
FLAG | 0.135 | 0.161 | 700 | 0.964 | 4 | 61/0 | 0.1071 | 12900 | 0.5495 | 24 | 656.8 | 9999 | 1 | 0
POPPY | 0.882 | 1.057 | 105.6 | 0.368 | 4 | 7/0 | 0.1228 | 1990 | 0.0829 | 6 | 99.1 | 9999 | 1 | 0
PANSY/T2 | 0.5571 | 0.6672 | 167.4 | 0.537 | 4 | 7/0 | 0.1093 | 3280 | 0.1314 | 6 | 156.9 | 9999 | 1 | 0
PANSY | 1.114 | 1.334 | 83.69 | 0.328 | 4 | 7/0 | 0.1093 | 1640 | 0.0657 | 6 | 78.5 | 9999 | 1 | 0
OXLIP/T2 | 0.2214 | 0.2647 | 423.2 | 0.855 | 4 | 7/0 | 0.1739 | 7660 | 0.3324 | 6 | 397.2 | 9999 | 1 | 0
OXLIP | 0.441 | 0.528 | 211.6 | 0.522 | 4 | 7/0 | 0.1739 | 3830 | 0.1663 | 6 | 198.7 | 9999 | 1 | 0
PEACHBELL | 3.551 | 4.255 | 26.24 | 0.184 | 4 | 7/0 | 0.0612 | 563 | 0.0206 | 6 | 24.6 | 9999 | 1 | 0
PLUTO | 0.2693 | 0.2704 | 406.55 | 0.74 | 4 | 19/0 | 0.1476 | 7261.3282 | 0.3252 | 19 | 388.3987 | 9999 | 1 | 0
VIRGO | 0.0393 | 0.0439 | 2782.66 | 1.949 | 4 | 91/0 | 0.1772 | 46535 | 2.2429 | 30 | 2694.6 | 9999 | 1 | 0
PEONY | 0.311 | 0.372 | 300 | 0.629 | 4 | 19/0 | 0.1257 | 5480 | 0.2358 | 12 | 281.8 | 9999 | 1 | 0
ORCHID | 0.149 | 0.177 | 636 | 0.918 | 4 | 37/0 | 0.1311 | 11400 | 0.4995 | 18 | 596.9 | 9999 | 1 | 0
POPPY/T2 | 0.4418 | 0.529 | 211.2 | 0.602 | 4 | 7/0 | 0.1228 | 3980 | 0.1658 | 6 | 198.1 | 9999 | 1 | 0
NEPTUNE | 0.3598 | 0.3605 | 305.9 | 0.642 | 4 | 19/0 | 0.128 | 5552.7804 | 0.2443 | 19 | 290.963 | 9999 | 1 | 0
PHLOX | 0.556 | 0.665 | 167.8 | 0.464 | 4 | 7/0 | 0.1548 | 3040 | 0.1317 | 6 | 157.5 | 9999 | 1 | 0
NASTURTIUM | 0.133 | 0.158 | 715.5 | 0.975 | 4 | 61/0 | 0.1083 | 13100 | 0.5619 | 24 | 671.6 | 9999 | 1 | 0
NARCISSUS | 0.0772 | 0.0911 | 1272 | 1.3 | 4 | 61/0 | 0.1444 | 22000 | 0.999 | 24 | 1194 | 9999 | 1 | 0
PHLOX/T2 | 0.2785 | 0.3333 | 335.6 | 0.76 | 4 | 7/0 | 0.1548 | 6080 | 0.2636 | 6 | 314.8 | 9999 | 1 | 0
MOON | 0.4561 | 0.457 | 240.77 | 0.563 | 4 | 7/0 | 0.187 | 4226.4078 | 0.1922 | 7 | 228.4698 | 9999 | 1 | 0
MISTLETOE | 0.169 | 0.202 | 556.5 | 0.858 | 4 | 37/0 | 0.1226 | 9940 | 0.4368 | 18 | 522 | 9999 | 1 | 0
MERCURY | 0.5072 | 0.5069 | 217.09 | 0.531 | 4 | 7/0 | 0.1772 | 3776.7899 | 0.1725 | 7 | 204.9509 | 9999 | 1 | 0
MEADOWSWEET | 0.157 | 0.188 | 600 | 0.891 | 4 | 37/0 | 0.1273 | 10700 | 0.4709 | 18 | 562.8 | 9999 | 1 | 0
MARS | 0.7274 | 0.7274 | 150.58 | 0.445 | 4 | 7/0 | 0.1476 | 2675.2262 | 0.1198 | 7 | 142.4576 | 9999 | 1 | 0
DAISY/T2 | 0.1763 | 0.2105 | 533.6 | 0.959 | 4 | 7/0 | 0.1953 | 9700 | 0.419 | 6 | 501 | 9999 | 1 | 0
ZINNIA | 0.188 | 0.225 | 500 | 0.811 | 4 | 19/0 | 0.1622 | 8760 | 0.3926 | 12 | 469.2 | 9999 | 1 | 0
WASP | 0.5289 | 0.5504 | 207.61 | 0.519 | 4 | 7/0 | 0.1728 | 3700 | 0.1646 | 7 | 194.9 | 9999 | 1 | 0
KAKI | 2.18 | 9999 | 49 | 0.25 | 5 | 7/0 | 0.0834 | 1430 | 0.0382 | 6 | 45.7 | 9999 | 1 | 0
REDE | 0.254 | 9999 | 420 | 0.743 | 5 | 19/0 | 0.1486 | 11200 | 0.3295 | 12 | 393.9 | 9999 | 1 | 0
REMEX | 0.192 | 9999 | 559 | 0.858 | 5 | 19/0 | 0.1716 | 13900 | 0.4394 | 12 | 525.2 | 9999 | 1 | 0
RADAR | 0.3 | 9999 | 355 | 0.683 | 5 | 19/0 | 0.1368 | 9600 | 0.2789 | 12 | 333.3 | 9999 | 1 | 0
RADIAN | 0.27 | 9999 | 395 | 0.721 | 5 | 19/0 | 0.1442 | 10500 | 0.3099 | 12 | 370.3 | 9999 | 1 | 0
RAGOUT | 0.23 | 9999 | 465 | 0.782 | 5 | 19/0 | 0.1566 | 12200 | 0.3655 | 12 | 436.9 | 9999 | 1 | 0
RATCH | 0.378 | 9999 | 281 | 0.608 | 5 | 19/0 | 0.1218 | 7610 | 0.221 | 12 | 264.2 | 9999 | 1 | 0
KAYAK | 0.684 | 9999 | 155 | 0.447 | 5 | 7/0 | 0.149 | 4280 | 0.1221 | 6 | 145.9 | 9999 | 1 | 0
KAZOO | 3.47 | 9999 | 31 | 0.198 | 5 | 7/0 | 0.0661 | 922 | 0.024 | 6 | 28.7 | 9999 | 1 | 0
KENCH | 1.37 | 9999 | 77 | 0.316 | 5 | 7/0 | 0.1052 | 2220 | 0.0608 | 6 | 72.7 | 9999 | 1 | 0
KIBE | 0.862 | 9999 | 123 | 0.398 | 5 | 7/0 | 0.1327 | 3440 | 0.0968 | 6 | 115.7 | 9999 | 1 | 0
KITTLE | 0.431 | 9999 | 247 | 0.563 | 5 | 7/0 | 0.1878 | 6330 | 0.1939 | 6 | 231.8 | 9999 | 1 | 0
RAMIE | 0.341 | 9999 | 313 | 0.642 | 5 | 19/0 | 0.1284 | 8450 | 0.2456 | 12 | 293.6 | 9999 | 1 | 0
SOLAR | 0.117 | 9999 | 927 | 1.108 | 5 | 37/0 | 0.1583 | 23900 | 0.7282 | 18 | 870.4 | 9999 | 1 | 0
REX | 0.212 | 9999 | 504 | 0.814 | 5 | 19/0 | 0.1628 | 12500 | 0.3955 | 12 | 472.7 | 9999 | 1 | 0
RUBLE | 0.183 | 9999 | 587 | 0.879 | 5 | 19/0 | 0.1758 | 14600 | 0.4612 | 12 | 551.2 | 9999 | 1 | 0
RUNE | 0.165 | 9999 | 652 | 0.926 | 5 | 19/0 | 0.1854 | 16200 | 0.5124 | 12 | 612.4 | 9999 | 1 | 0
KOPECK | 0.544 | 9999 | 196 | 0.502 | 5 | 7/0 | 0.1672 | 5020 | 0.1537 | 6 | 183.7 | 9999 | 1 | 0
SPAR | 0.146 | 9999 | 741 | 0.99 | 5 | 37/0 | 0.1416 | 19300 | 0.5818 | 18 | 695.4 | 9999 | 1 | 0
SPINEL | 0.1276 | 0.1294 | 842.69 | 1.154 | 6 | 61/0 | 0.128 | 30349 | 0.7843 | 24 | 940.8 | 9999 | 1 | 0
OPAL | 0.4087 | 0.4088 | 264.45 | 0.642 | 6 | 19/0 | 0.128 | 9937 | 0.2443 | 12 | 291 | 9999 | 1 | 0
TOPAZ | 0.096 | 0.0982 | 1122.93 | 1.331 | 6 | 61/0 | 0.1476 | 40241 | 1.0442 | 24 | 1249.9 | 9999 | 1 | 0
JADE | 0.5745 | 0.5745 | 187.09 | 0.531 | 6 | 7/0 | 0.1772 | 7014 | 0.1725 | 6 | 204.3 | 9999 | 1 | 0
ALLIANCE | 0.439 | 0.514 | 247 | 0.563 | 6 | 7/0 | 0.1878 | 8560 | 0.1939 | 6 | 231.8 | 9999 | 1 | 0
AMETHYST | 2.2943 | 2.3013 | 46.77 | 0.266 | 6 | 7/0 | 0.0886 | 1749 | 0.0431 | 6 | 51 | 9999 | 1 | 0
AKRON | 3.54 | 4.14 | 31 | 0.198 | 6 | 7/0 | 0.0661 | 1110 | 0.024 | 6 | 28.7 | 9999 | 1 | 0
AGATE | 3.798 | 3.7979 | 28.22 | 0.207 | 6 | 7/0 | 0.0689 | 1059 | 0.0261 | 6 | 31 | 9999 | 1 | 0
ZIRCON | 0.0447 | 0.0491 | 2407.69 | 1.949 | 6 | 91/0 | 0.1772 | 86327 | 2.2429 | 30 | 2687.9 | 9999 | 1 | 0
BUTTE | 0.347 | 0.406 | 313 | 0.642 | 6 | 19/0 | 0.1283 | 11000 | 0.2456 | 12 | 293.6 | 9999 | 1 | 0
PEARL | 0.3065 | 0.3058 | 351.29 | 0.74 | 6 | 19/0 | 0.1476 | 13219 | 0.3252 | 12 | 387.1 | 9999 | 1 | 0
AMES | 1.4 | 1.64 | 77 | 0.316 | 6 | 7/0 | 0.1052 | 2800 | 0.0608 | 6 | 72.7 | 9999 | 1 | 0
CAIRO | 0.234 | 0.273 | 465 | 0.782 | 6 | 19/0 | 0.1565 | 15600 | 0.3655 | 12 | 436.9 | 9999 | 1 | 0
AMHERST | 0.554 | 0.648 | 196 | 0.502 | 6 | 7/0 | 0.1672 | 6790 | 0.1537 | 6 | 183.7 | 9999 | 1 | 0
ANAHEIM | 0.697 | 0.816 | 155 | 0.447 | 6 | 7/0 | 0.149 | 5390 | 0.1221 | 6 | 145.9 | 9999 | 1 | 0
CANTON | 0.276 | 0.322 | 395 | 0.721 | 6 | 19/0 | 0.1441 | 13300 | 0.3099 | 12 | 370.3 | 9999 | 1 | 0
SAPPHIRE | 0.1579 | 0.1595 | 682.84 | 1.035 | 6 | 37/0 | 0.1476 | 25853 | 0.6335 | 18 | 752.6 | 9999 | 1 | 0
RUTILE | 0.1911 | 0.1931 | 562.45 | 0.937 | 6 | 19/0 | 0.187 | 21222 | 0.5219 | 12 | 620.9 | 9999 | 1 | 0
AZUSA | 0.878 | 1.028 | 123 | 0.398 | 6 | 7/0 | 0.1327 | 4460 | 0.0968 | 6 | 115.7 | 9999 | 1 | 0
RUBY | 0.2468 | 0.2462 | 436.15 | 0.827 | 6 | 37/0 | 0.1181 | 16523 | 0.4053 | 18 | 484.5 | 9999 | 1 | 0
ALTON | 2.22 | 2.6 | 49 | 0.25 | 6 | 7/0 | 0.0834 | 1760 | 0.0382 | 6 | 45.7 | 9999 | 1 | 0
DIAMOND | 1.8643 | 1.8668 | 57.82 | 0.295 | 6 | 7/0 | 0.0984 | 2167 | 0.0533 | 6 | 63.4 | 9999 | 1 | 0
GARNET | 0.829 | 0.8288 | 129.86 | 0.445 | 6 | 7/0 | 0.1476 | 4878 | 0.1198 | 6 | 141.8 | 9999 | 1 | 0
GREELEY | 0.119 | 0.139 | 927 | 1.108 | 6 | 37/0 | 0.1583 | 30500 | 0.7282 | 18 | 870.4 | 9999 | 1 | 0
ELGIN | 0.168 | 0.196 | 652 | 0.926 | 6 | 19/0 | 0.1853 | 21900 | 0.5124 | 12 | 612.4 | 9999 | 1 | 0
EMERALD | 1.2936 | 1.2939 | 83.09 | 0.354 | 6 | 7/0 | 0.1181 | 3125 | 0.0767 | 6 | 90.7 | 9999 | 1 | 0
JASPER | 0.5167 | 0.5166 | 209.19 | 0.563 | 6 | 7/0 | 0.187 | 7823 | 0.1922 | 6 | 227.8 | 9999 | 1 | 0
FLINT | 0.148 | 0.173 | 741 | 0.99 | 6 | 37/0 | 0.1415 | 24400 | 0.5818 | 18 | 695.4 | 9999 | 1 | 0
DARIEN | 0.195 | 0.228 | 559 | 0.858 | 6 | 19/0 | 0.1716 | 18800 | 0.4394 | 12 | 525.2 | 9999 | 1 | 0
DOVE2 | 0.1525 | 9999 | 653 | 0.927 | 7 | 12/7 | 0.1854 | 16100 | 0.5129 | 12 | 613 | 9999 | 1 | 0
BLUEJAY3 | 0.0871 | 9999 | 1197 | 1.259 | 7 | 18/19 | 0.1799 | 32300 | 0.94 | 18 | 1124 | 9999 | 1 | 0
RAIL3 | 0.1006 | 9999 | 1024 | 1.165 | 7 | 18/19 | 0.1664 | 27700 | 0.8046 | 18 | 961.7 | 9999 | 1 | 0
RAIL4 | 0.0998 | 9999 | 1012 | 1.158 | 7 | 24/13 | 0.1654 | 24700 | 0.8046 | 18 | 950 | 9999 | 1 | 0
RAIL5 | 0.101 | 9999 | 983 | 1.141 | 7 | 30/7 | 0.163 | 21500 | 0.8046 | 18 | 923 | 9999 | 1 | 0
DRAKE2 | 0.1087 | 9999 | 927 | 1.108 | 7 | 24/13 | 0.1583 | 22600 | 0.7282 | 18 | 870.4 | 9999 | 1 | 0
DRAKE1 | 0.1058 | 9999 | 927 | 1.108 | 7 | 30/7 | 0.1583 | 20300 | 0.7282 | 18 | 870.4 | 9999 | 1 | 0
DOVE1 | 0.1488 | 9999 | 653 | 0.927 | 7 | 15/4 | 0.1854 | 14500 | 0.5129 | 12 | 613 | 9999 | 1 | 0
BUNTING1 | 0.0788 | 9999 | 1280 | 1.302 | 7 | 30/7 | 0.186 | 28000 | 1.005 | 18 | 1201 | 9999 | 1 | 0
CURLEW2 | 0.0854 | 9999 | 1172 | 1.246 | 7 | 30/7 | 0.178 | 25600 | 0.92 | 18 | 1100 | 9999 | 1 | 0
PELICAN1 | 0.1925 | 9999 | 504 | 0.814 | 7 | 15/4 | 0.1628 | 11200 | 0.395 | 12 | 472.1 | 9999 | 1 | 0
BLUEJAY2 | 0.0852 | 9999 | 1197 | 1.259 | 7 | 24/13 | 0.1799 | 29300 | 0.94 | 18 | 1124 | 9999 | 1 | 0
DRAKE3 | 0.1117 | 9999 | 927 | 1.108 | 7 | 18/19 | 0.1583 | 23300 | 0.7282 | 18 | 870.4 | 9999 | 1 | 0
CURLEW1 | 0.0845 | 9999 | 1172 | 1.246 | 7 | 33/4 | 0.178 | 23100 | 0.92 | 18 | 1100 | 9999 | 1 | 0
CURLEW4 | 0.0892 | 9999 | 1172 | 1.246 | 7 | 18/19 | 0.178 | 31600 | 0.92 | 18 | 1100 | 9999 | 1 | 0
CURLEW3 | 0.0872 | 9999 | 1172 | 1.246 | 7 | 24/13 | 0.178 | 28600 | 0.92 | 18 | 1100 | 9999 | 1 | 0
BITTERN1 | 0.0739 | 9999 | 1362 | 1.345 | 7 | 54/7 | 0.1491 | 27500 | 1.07 | 24 | 1278 | 9999 | 1 | 0
BLUEBIRD3 | 0.0465 | 9999 | 2339 | 1.762 | 7 | 42/19 | 0.1958 | 55000 | 1.837 | 24 | 2194 | 9999 | 1 | 0
PELICAN2 | 0.1964 | 9999 | 504 | 0.814 | 7 | 12/7 | 0.1628 | 12400 | 0.395 | 12 | 473 | 9999 | 1 | 0
TERN3 | 0.1204 | 9999 | 854 | 1.063 | 7 | 18/19 | 0.1519 | 23000 | 0.6705 | 18 | 801.4 | 9999 | 1 | 0
KIWI3 | 0.048 | 9999 | 2267 | 1.735 | 7 | 42/19 | 0.1928 | 53300 | 1.781 | 24 | 2127 | 9999 | 1 | 0
BITTERN2 | 0.0757 | 9999 | 1362 | 1.345 | 7 | 42/19 | 0.1494 | 32800 | 1.07 | 24 | 1278 | 9999 | 1 | 0
ORTOLAN3 | 0.0937 | 9999 | 1109 | 1.212 | 7 | 18/19 | 0.1731 | 29900 | 0.871 | 18 | 1041 | 9999 | 1 | 0
ORTOLAN2 | 0.0917 | 9999 | 1109 | 1.212 | 7 | 24/13 | 0.1731 | 27000 | 0.871 | 18 | 1041 | 9999 | 1 | 0
ORTOLAN1 | 0.0897 | 9999 | 1109 | 1.212 | 7 | 30/7 | 0.1731 | 24200 | 0.871 | 18 | 1041 | 9999 | 1 | 0
RAIL2 | 0.0986 | 9999 | 1024 | 1.165 | 7 | 24/13 | 0.1664 | 25000 | 0.8046 | 18 | 961.7 | 9999 | 1 | 0
BLUEBIRD2 | 0.046 | 9999 | 2339 | 1.762 | 7 | 48/13 | 0.1958 | 51600 | 1.837 | 24 | 2194 | 9999 | 1 | 0
BLUEJAY1 | 0.0834 | 9999 | 1197 | 1.259 | 7 | 30/7 | 0.1799 | 26200 | 0.94 | 18 | 1124 | 9999 | 1 | 0
DRAKE6 | 0.1192 | 9999 | 819 | 1.042 | 7 | 30/7 | 0.1488 | 18100 | 0.7282 | 18 | 769 | 9999 | 1 | 0
MERLIN2 | 0.278 | 9999 | 355 | 0.683 | 7 | 12/7 | 0.1367 | 8900 | 0.2789 | 12 | 333 | 9999 | 1 | 0
MERLIN1 | 0.2711 | 9999 | 355 | 0.683 | 7 | 15/4 | 0.1367 | 8100 | 0.2789 | 12 | 333.3 | 9999 | 1 | 0
DRAKE5 | 0.1192 | 9999 | 840 | 1.055 | 7 | 24/13 | 0.1507 | 20500 | 0.7282 | 18 | 789 | 9999 | 1 | 0
BUNTING2 | 0.0805 | 9999 | 1280 | 1.302 | 7 | 24/13 | 0.186 | 31300 | 1.005 | 18 | 1201 | 9999 | 1 | 0
RAIL1 | 0.0965 | 9999 | 1024 | 1.165 | 7 | 30/7 | 0.1664 | 22400 | 0.8046 | 18 | 961.7 | 9999 | 1 | 0
BUNTING3 | 0.0823 | 9999 | 1280 | 1.302 | 7 | 18/19 | 0.186 | 34500 | 1.005 | 18 | 1201 | 9999 | 1 | 0
BLUEBIRD1 | 0.0454 | 9999 | 2339 | 1.762 | 7 | 54/7 | 0.1958 | 46100 | 1.837 | 24 | 2194 | 9999 | 1 | 0
GROSBEAK3 | 0.1348 | 9999 | 740 | 0.99 | 7 | 24/13 | 0.1414 | 18300 | 0.5812 | 18 | 695 | 9999 | 1 | 0
CARDINAL1 | 0.092 | 9999 | 1081 | 1.196 | 7 | 30/7 | 0.1709 | 23600 | 0.8487 | 18 | 1015 | 9999 | 1 | 0
CARDINAL2 | 0.094 | 9999 | 1081 | 1.196 | 7 | 24/13 | 0.1709 | 26400 | 0.8487 | 18 | 1015 | 9999 | 1 | 0
CARDINAL3 | 0.0962 | 9999 | 1081 | 1.196 | 7 | 18/19 | 0.1709 | 29200 | 0.8487 | 18 | 1015 | 9999 | 1 | 0
TERN1 | 0.1144 | 9999 | 854 | 1.063 | 7 | 30/7 | 0.1519 | 18600 | 0.6705 | 18 | 801.4 | 9999 | 1 | 0
TERN2 | 0.1175 | 9999 | 854 | 1.063 | 7 | 24/13 | 0.1519 | 20800 | 0.6705 | 18 | 801.4 | 9999 | 1 | 0
GROSBEAK2 | 0.1318 | 9999 | 740 | 0.99 | 7 | 30/7 | 0.1414 | 16400 | 0.5812 | 18 | 695 | 9999 | 1 | 0
CHAMERA | 0.0877 | 9999 | 1160 | 1.24 | 7 | 30/7 | 0.1772 | 26078 | 0.9114 | 18 | 1091.3 | 9999 | 1 | 0
GROSBEAK4 | 0.1378 | 9999 | 740 | 0.99 | 7 | 18/19 | 0.1414 | 20100 | 0.5812 | 18 | 695 | 9999 | 1 | 0
LAPWING2 | 0.0615 | 9999 | 1703 | 1.504 | 7 | 48/13 | 0.1671 | 37900 | 1.338 | 24 | 1599 | 9999 | 1 | 0
KIWI2 | 0.0475 | 9999 | 2267 | 1.735 | 7 | 48/13 | 0.1928 | 50000 | 1.781 | 24 | 2127 | 9999 | 1 | 0
GROSBEAK1 | 0.1297 | 9999 | 740 | 0.99 | 7 | 33/4 | 0.1414 | 14900 | 0.5812 | 18 | 695 | 9999 | 1 | 0
LAPWING1 | 0.0608 | 9999 | 1703 | 1.504 | 7 | 54/7 | 0.1671 | 35200 | 1.338 | 24 | 1599 | 9999 | 1 | 0
KIWI1 | 0.0468 | 9999 | 2267 | 1.735 | 7 | 54/7 | 0.1928 | 44800 | 1.781 | 24 | 2127 | 9999 | 1 | 0
LAPWING3 | 0.0623 | 9999 | 1703 | 1.504 | 7 | 42/19 | 0.1671 | 40500 | 1.338 | 24 | 1599 | 9999 | 1 | 0
CHUKAR1 | 0.0544 | 9999 | 1933 | 1.602 | 7 | 54/7 | 0.178 | 39900 | 1.518 | 24 | 1814 | 9999 | 1 | 0
CHUKAR2 | 0.055 | 9999 | 1933 | 1.602 | 7 | 48/13 | 0.178 | 43000 | 1.518 | 24 | 1814 | 9999 | 1 | 0
CHUKAR3 | 0.0557 | 9999 | 1933 | 1.602 | 7 | 42/19 | 0.178 | 46000 | 1.518 | 24 | 1814 | 9999 | 1 | 0
3#10AW | 8.87 | 10.467 | 31.2 | 0.22 | 8 | 3/0 | 0.0733 | 4532 | 0.0245 | 3 | 70.4 | 9999 | 1 | 0
19#8AW | 0.904 | 1.066 | 313.7 | 0.642 | 8 | 19/0 | 0.1284 | 43240 | 0.2464 | 12 | 713.5 | 9999 | 1 | 0
19#5AW | 0.451 | 0.532 | 628.7 | 0.91 | 8 | 19/0 | 0.182 | 73350 | 0.494 | 12 | 1430 | 9999 | 1 | 0
7#5AW | 1.24 | 1.463 | 231.6 | 0.546 | 8 | 7/0 | 0.182 | 27030 | 0.182 | 6 | 524.9 | 9999 | 1 | 0
19#7AW | 0.717 | 0.846 | 395.6 | 0.721 | 8 | 19/0 | 0.1442 | 51730 | 0.3107 | 12 | 899.5 | 9999 | 1 | 0
19#9AW | 1.14 | 1.345 | 248.7 | 0.572 | 8 | 19/0 | 0.1144 | 34290 | 0.1954 | 12 | 565.8 | 9999 | 1 | 0
19#10AW | 1.437 | 1.696 | 197.3 | 0.509 | 8 | 19/0 | 0.1018 | 27190 | 0.1549 | 12 | 448.7 | 9999 | 1 | 0
7#8AW | 2.44 | 2.879 | 115.6 | 0.385 | 8 | 7/0 | 0.128 | 15930 | 0.0908 | 6 | 261.8 | 9999 | 1 | 0
7#10AW | 3.88 | 4.578 | 72.7 | 0.306 | 8 | 7/0 | 0.102 | 10020 | 0.0571 | 6 | 164.7 | 9999 | 1 | 0
37#9AW | 0.589 | 0.695 | 484.2 | 0.801 | 8 | 37/0 | 0.1144 | 66770 | 0.3805 | 18 | 1108 | 9999 | 1 | 0
37#8AW | 0.467 | 0.551 | 611 | 0.899 | 8 | 37/0 | 0.1284 | 84200 | 0.4798 | 18 | 1398 | 9999 | 1 | 0
37#7AW | 0.233 | 0.275 | 770.4 | 1.01 | 8 | 37/0 | 0.1443 | 100700 | 0.605 | 18 | 1762 | 9999 | 1 | 0
37#6AW | 0.294 | 0.346 | 971 | 1.134 | 8 | 37/0 | 0.1614 | 120200 | 0.7629 | 18 | 2222 | 9999 | 1 | 0
7#6AW | 1.536 | 1.812 | 183.7 | 0.486 | 8 | 7/0 | 0.162 | 22730 | 0.1443 | 6 | 416.3 | 9999 | 1 | 0
19#6AW | 0.568 | 0.671 | 498.6 | 0.81 | 8 | 19/0 | 0.162 | 61700 | 0.3917 | 12 | 1134 | 9999 | 1 | 0
7#7AW | 1.937 | 2.286 | 145.8 | 0.433 | 8 | 7/0 | 0.144 | 19060 | 0.1145 | 6 | 330 | 9999 | 1 | 0
3#5AW | 2.78 | 3.28 | 99.3 | 0.392 | 8 | 3/0 | 0.1307 | 12230 | 0.078 | 3 | 224.5 | 9999 | 1 | 0
7#9AW | 3.08 | 3.634 | 91.6 | 0.343 | 8 | 7/0 | 0.114 | 12630 | 0.072 | 6 | 207.6 | 9999 | 1 | 0
3#9AW | 7.04 | 8.307 | 39.3 | 0.246 | 8 | 3/0 | 0.0823 | 5715 | 0.0308 | 3 | 88.8 | 9999 | 1 | 0
3#6AW | 3.51 | 4.142 | 78.7 | 0.349 | 8 | 3/0 | 0.1163 | 10280 | 0.0618 | 3 | 178.1 | 9999 | 1 | 0
3#7AW | 4.42 | 5.216 | 62.5 | 0.311 | 8 | 3/0 | 0.1037 | 8621 | 0.049 | 3 | 141.2 | 9999 | 1 | 0
3#8AW | 5.58 | 6.584 | 49.5 | 0.277 | 8 | 3/0 | 0.0923 | 7206 | 0.0389 | 3 | 112 | 9999 | 1 | 0
37#5AW | 0.233 | 0.275 | 1224.2 | 1.273 | 8 | 37/0 | 0.1814 | 142800 | 0.9619 | 18 | 2802 | 9999 | 1 | 0
37#10AW | 0.741 | 0.874 | 384.2 | 0.713 | 8 | 37/0 | 0.1019 | 52950 | 0.3017 | 18 | 879 | 9999 | 1 | 0
1/2EHS | 3.66 | 4.246 | 0 | 0.495 | 9 | 7/0 | 0.165 | 26900 | 0.1497 | 6 | 517 | 9999 | 1 | 0
5/8EHS | 2.32 | 2.691 | 0 | 0.621 | 9 | 7/0 | 0.207 | 42400 | 0.2355 | 6 | 813 | 9999 | 1 | 0
5/8HS | 2.27 | 2.633 | 0 | 0.621 | 9 | 7/0 | 0.207 | 29600 | 0.2355 | 6 | 813 | 9999 | 1 | 0
7/16EHS | 4.74 | 5.498 | 0 | 0.435 | 9 | 7/0 | 0.145 | 20800 | 0.1156 | 6 | 399 | 9999 | 1 | 0
5/16EHS | 9.2 | 10.672 | 0 | 0.312 | 9 | 7/0 | 0.104 | 11200 | 0.0595 | 6 | 205 | 9999 | 1 | 0
1/2HS | 3.57 | 4.141 | 0 | 0.495 | 9 | 7/0 | 0.165 | 18800 | 0.1497 | 6 | 517 | 9999 | 1 | 0
7/16HS | 4.62 | 5.359 | 0 | 0.435 | 9 | 7/0 | 0.145 | 14500 | 0.1156 | 6 | 399 | 9999 | 1 | 0
3/8EHS | 6.93 | 8.039 | 0 | 0.36 | 9 | 7/0 | 0.12 | 15400 | 0.0792 | 6 | 273 | 9999 | 1 | 0
3/8HS | 6.75 | 7.83 | 0 | 0.36 | 9 | 7/0 | 0.12 | 10800 | 0.0792 | 6 | 273 | 9999 | 1 | 0
CU8AWG-1 | 3.5141 | 4.1676 | 16.51 | 0.1285 | 10 | 1/0 | 0.1285 | 826 | 0.013 | 1 | 50 | 9999 | 1 | 0
CU900-37 | 0.0702 | 0.0818 | 900 | 1.092 | 10 | 37/0 | 0.156 | 39500 | 0.7072 | 18 | 2780.1 | 9999 | 1 | 0
CU900-61 | 0.0702 | 0.0818 | 900 | 1.0935 | 10 | 61/0 | 0.1215 | 40500 | 0.7072 | 24 | 2780.3 | 9999 | 1 | 0
CU800-37 | 0.078 | 0.0911 | 800 | 1.029 | 10 | 37/0 | 0.147 | 35100 | 0.628 | 18 | 2468.6 | 9999 | 1 | 0
CU800-61 | 0.078 | 0.0911 | 800 | 1.0305 | 10 | 61/0 | 0.1145 | 36300 | 0.6281 | 24 | 2469.2 | 9999 | 1 | 0
CU300-37 | 0.1988 | 0.2353 | 300 | 0.63 | 10 | 37/0 | 0.09 | 13900 | 0.2354 | 18 | 925.3 | 9999 | 1 | 0
CU1AWG-3 | 0.7007 | 0.8309 | 83.69 | 0.3599 | 10 | 3/0 | 0.167 | 3620 | 0.0657 | 3 | 255.9 | 9999 | 1 | 0
CU4/0AWG-12 | 0.2808 | 0.3326 | 211.6 | 0.5518 | 10 | 12/0 | 0.1328 | 9480 | 0.1662 | 6 | 653.4 | 9999 | 1 | 0
CU4/0AWG-1 | 0.273 | 0.3237 | 211.6 | 0.46 | 10 | 1/0 | 0.46 | 8140 | 0.1662 | 1 | 641 | 9999 | 1 | 0
CU3AWG-7 | 1.1248 | 1.3339 | 52.63 | 0.2601 | 10 | 7/0 | 0.0867 | 2430 | 0.0413 | 6 | 162.5 | 9999 | 1 | 0
CU3AWG-3 | 1.114 | 1.3211 | 52.63 | 0.2855 | 10 | 3/0 | 0.1325 | 2360 | 0.0414 | 3 | 160.9 | 9999 | 1 | 0
CU3AWG-1 | 1.103 | 1.308 | 52.63 | 0.2294 | 10 | 1/0 | 0.2294 | 2440 | 0.0413 | 1 | 159 | 9999 | 1 | 0
CU350-37 | 0.1709 | 0.2021 | 350 | 0.6811 | 10 | 37/0 | 0.0973 | 16100 | 0.2751 | 18 | 1081.5 | 9999 | 1 | 0
CU350-19 | 0.1709 | 0.2021 | 350 | 0.6785 | 10 | 19/0 | 0.1357 | 15600 | 0.2748 | 12 | 1080.3 | 9999 | 1 | 0
CU350-12 | 0.1709 | 0.2021 | 350 | 0.7097 | 10 | 12/0 | 0.1708 | 15100 | 0.2749 | 6 | 1080.9 | 9999 | 1 | 0
CU1AWG-7 | 0.7076 | 0.8391 | 83.69 | 0.3279 | 10 | 7/0 | 0.1093 | 3800 | 0.0657 | 6 | 258.4 | 9999 | 1 | 0
CU2/0AWG-1 | 0.4329 | 0.5136 | 133.1 | 0.3648 | 10 | 1/0 | 0.3648 | 5520 | 0.1045 | 1 | 403 | 9999 | 1 | 0
CU2AWG-1 | 0.8747 | 1.0373 | 66.37 | 0.2576 | 10 | 1/0 | 0.2576 | 3000 | 0.0521 | 1 | 201 | 9999 | 1 | 0
CU2/0AWG-7 | 0.4454 | 0.5279 | 133.1 | 0.4137 | 10 | 7/0 | 0.1379 | 5930 | 0.1045 | 6 | 411 | 9999 | 1 | 0
CU4/0AWG-7 | 0.2808 | 0.3326 | 211.6 | 0.5217 | 10 | 7/0 | 0.1739 | 9160 | 0.1663 | 6 | 653.3 | 9999 | 1 | 0
CU300-19 | 0.1988 | 0.2353 | 300 | 0.6285 | 10 | 19/0 | 0.1257 | 13500 | 0.2358 | 12 | 926.9 | 9999 | 1 | 0
CU7AWG-1 | 2.7868 | 3.305 | 20.82 | 0.1443 | 10 | 1/0 | 0.1443 | 1030 | 0.0164 | 1 | 63 | 9999 | 1 | 0
CU250-12 | 0.238 | 0.2819 | 250 | 0.5996 | 10 | 12/0 | 0.1443 | 11100 | 0.1962 | 6 | 771.5 | 9999 | 1 | 0
CU700-61 | 0.0881 | 0.1033 | 700 | 0.9639 | 10 | 61/0 | 0.1071 | 31800 | 0.5495 | 24 | 2160.3 | 9999 | 1 | 0
CU250-19 | 0.238 | 0.2819 | 250 | 0.5735 | 10 | 19/0 | 0.1147 | 11400 | 0.1963 | 12 | 771.8 | 9999 | 1 | 0
CU250-37 | 0.238 | 0.2819 | 250 | 0.5754 | 10 | 37/0 | 0.0822 | 11600 | 0.1964 | 18 | 771.9 | 9999 | 1 | 0
CU3/0AWG-7 | 0.3536 | 0.419 | 167.8 | 0.4644 | 10 | 7/0 | 0.1548 | 7360 | 0.1317 | 6 | 517.9 | 9999 | 1 | 0
CU3/0AWG-19 | 0.3536 | 0.419 | 167.8 | 0.452 | 10 | 19/0 | 0.0904 | 7180 | 0.1219 | 12 | 479.4 | 9999 | 1 | 0
CU3/0AWG-12 | 0.3536 | 0.419 | 167.8 | 0.4915 | 10 | 12/0 | 0.1183 | 7560 | 0.1319 | 6 | 518.5 | 9999 | 1 | 0
CU3/0AWG-1 | 0.3437 | 0.4077 | 167.8 | 0.4096 | 10 | 1/0 | 0.4096 | 6720 | 0.1318 | 1 | 508 | 9999 | 1 | 0
CU2AWG-7 | 0.8921 | 1.0579 | 66.37 | 0.2922 | 10 | 7/0 | 0.0974 | 3050 | 0.0522 | 6 | 204.9 | 9999 | 1 | 0
CU2AWG-3 | 0.8835 | 1.0477 | 66.37 | 0.3204 | 10 | 3/0 | 0.1487 | 2910 | 0.0521 | 3 | 202.9 | 9999 | 1 | 0
CU2/0AWG19 | 0.4454 | 0.5279 | 133.1 | 0.4185 | 10 | 19/0 | 0.0837 | 6150 | 0.1045 | 12 | 411 | 9999 | 1 | 0
CU1/0AWG-1 | 0.5459 | 0.6477 | 105.5 | 0.3249 | 10 | 1/0 | 0.3249 | 4520 | 0.0829 | 1 | 320 | 9999 | 1 | 0
CU750-61 | 0.0827 | 0.0968 | 750 | 0.9981 | 10 | 61/0 | 0.1109 | 34100 | 0.5892 | 24 | 2316.4 | 9999 | 1 | 0
CU750-37 | 0.0827 | 0.0968 | 750 | 0.9968 | 10 | 37/0 | 0.1424 | 33400 | 0.5893 | 18 | 2316.5 | 9999 | 1 | 0
CU700-37 | 0.0881 | 0.1033 | 700 | 0.9625 | 10 | 37/0 | 0.1375 | 31200 | 0.5494 | 18 | 2159.8 | 9999 | 1 | 0
CU6AWG-1 | 2.2114 | 2.6226 | 26.25 | 0.162 | 10 | 1/0 | 0.162 | 1280 | 0.0206 | 1 | 79 | 9999 | 1 | 0
CU600-61 | 0.1017 | 0.1196 | 600 | 0.8928 | 10 | 61/0 | 0.0992 | 27500 | 0.4715 | 24 | 1853.4 | 9999 | 1 | 0
CU600-37 | 0.1009 | 0.1187 | 600 | 0.8911 | 10 | 37/0 | 0.1273 | 27000 | 0.4709 | 18 | 1851.3 | 9999 | 1 | 0
CU5AWG-1 | 1.7532 | 2.0791 | 33.1 | 0.1819 | 10 | 1/0 | 0.1819 | 1590 | 0.026 | 1 | 100 | 9999 | 1 | 0
CU500-37 | 0.1209 | 0.1425 | 500 | 0.8134 | 10 | 37/0 | 0.1162 | 22500 | 0.3924 | 18 | 1542.5 | 9999 | 1 | 0
CU500-19 | 0.1209 | 0.1425 | 500 | 0.811 | 10 | 19/0 | 0.1622 | 21900 | 0.3926 | 12 | 1543.4 | 9999 | 1 | 0
CU4AWG-7 | 1.4181 | 1.6818 | 41.74 | 0.2316 | 10 | 7/0 | 0.0772 | 1940 | 0.0328 | 6 | 128.9 | 9999 | 1 | 0
CU4AWG-3 | 1.4042 | 1.6653 | 41.74 | 0.2543 | 10 | 3/0 | 0.118 | 1880 | 0.0328 | 3 | 127.6 | 9999 | 1 | 0
CU4AWG-1 | 1.3903 | 1.6488 | 41.74 | 0.2043 | 10 | 1/0 | 0.2043 | 1970 | 0.0328 | 1 | 126 | 9999 | 1 | 0
CU1AWG-1 | 0.6938 | 0.8226 | 83.69 | 0.2893 | 10 | 1/0 | 0.2893 | 3690 | 0.0657 | 1 | 253 | 9999 | 1 | 0
CU450-19 | 0.1338 | 0.1579 | 450 | 0.7695 | 10 | 19/0 | 0.1539 | 19800 | 0.3534 | 12 | 1389.5 | 9999 | 1 | 0
CU4/0AWG-19 | 0.2808 | 0.3326 | 211.6 | 0.5275 | 10 | 19/0 | 0.1055 | 9610 | 0.1661 | 12 | 652.9 | 9999 | 1 | 0
CU1/0AWG-19 | 0.5615 | 0.6658 | 105.5 | 0.3725 | 10 | 19/0 | 0.0745 | 4900 | 0.0828 | 12 | 325.6 | 9999 | 1 | 0
CU1/0AWG-7 | 0.5506 | 0.6658 | 105.5 | 0.3684 | 10 | 7/0 | 0.1228 | 4750 | 0.0829 | 6 | 325.9 | 9999 | 1 | 0
CU1000-37 | 0.064 | 0.0744 | 1000 | 1.1508 | 10 | 37/0 | 0.1644 | 43800 | 0.7854 | 18 | 3087.6 | 9999 | 1 | 0
CU1000-61 | 0.064 | 0.0744 | 1000 | 1.152 | 10 | 61/0 | 0.128 | 45000 | 0.7849 | 24 | 3085.8 | 9999 | 1 | 0
CU400-37 | 0.15 | 0.1772 | 400 | 0.728 | 10 | 37/0 | 0.104 | 18300 | 0.3143 | 18 | 1235.6 | 9999 | 1 | 0
CU400-19 | 0.15 | 0.1772 | 400 | 0.7255 | 10 | 19/0 | 0.1451 | 17800 | 0.3142 | 12 | 1235.1 | 9999 | 1 | 0
CU300-12 | 0.1988 | 0.2353 | 300 | 0.6569 | 10 | 12/0 | 0.1581 | 13200 | 0.2356 | 6 | 926.1 | 9999 | 1 | 0
CU450-37 | 0.1338 | 0.1579 | 450 | 0.7721 | 10 | 37/0 | 0.1103 | 20500 | 0.3535 | 18 | 1389.8 | 9999 | 1 | 0
1033-T13/3M/ACCR | 0.0882 | 0.1057 | 1033 | 1.24 | 11 | 54/19 | 0.138 | 35470 | 0.914 | 24 | 1130 | 0.0001 | 1 | 0
1113-T13/3M/ACCR | 0.0819 | 0.0981 | 1113 | 1.29 | 11 | 54/19 | 0.144 | 38217 | 0.985 | 24 | 1218 | 0.0001 | 1 | 0
1272-T13/3M/ACCR | 0.0717 | 0.0858 | 1272 | 1.38 | 11 | 54/19 | 0.153 | 43677 | 1.126 | 24 | 1392 | 0.0001 | 1 | 0
1351-T13/3M/ACCR | 0.0675 | 0.0808 | 1351 | 1.42 | 11 | 54/19 | 0.158 | 46389 | 1.195 | 24 | 1478 | 0.0001 | 1 | 0
1590-T13/3M/ACCR | 0.0573 | 0.0687 | 1590 | 1.54 | 11 | 54/19 | 0.172 | 54596 | 1.407 | 24 | 1740 | 0.0001 | 1 | 0
795-T16/3M/ACCR | 0.1126 | 0.1349 | 795 | 1.108 | 11 | 26/19 | 0.1749 | 31100 | 0.7238 | 16 | 896 | 0.0001 | 1 | 0
954-T13/3M/ACCR | 0.0955 | 0.1145 | 954 | 1.2 | 11 | 54/19 | 0.133 | 32758 | 0.844 | 24 | 1044 | 0.0001 | 1 | 0
636-T16/3M/ACCR | 0.1407 | 0.1686 | 636 | 0.99 | 11 | 26/19 | 0.156 | 25091 | 0.579 | 16 | 717 | 0.0001 | 1 | 0
556-T16/3M/ACCR | 0.1606 | 0.1924 | 556 | 0.93 | 11 | 26/7 | 0.146 | 22743 | 0.508 | 16 | 630 | 0.0001 | 1 | 0
477-T16/3M/ACCR | 0.1875 | 0.2247 | 477 | 0.86 | 11 | 26/7 | 0.135 | 19476 | 0.435 | 16 | 539 | 0.0001 | 1 | 0
336-T16/3M/ACCR | 0.2659 | 0.3185 | 336 | 0.72 | 11 | 26/7 | 0.114 | 13977 | 0.307 | 16 | 380 | 0.0001 | 1 | 0
397-T16/3M/ACCR | 0.225 | 0.2695 | 397 | 0.78 | 11 | 26/7 | 0.124 | 16398 | 0.363 | 16 | 449 | 0.0001 | 1 | 0
HAWK/ACCC/TW | 0.14951 | 0.1796 | 611 | 0.858 | 12 | 16/1 | 0.1964 | 23200 | 0.5415 | 10 | 623 | 0.28 | 1 | 0
BLUEBIRD/ACCC/TW | 0.03959 | 0.045544 | 2727 | 1.762 | 12 | 64/1 | 0.2065 | 59800 | 2.2777 | 23 | 2696 | 0.415 | 1 | 0
CHUCKAR/ACCC/TW | 0.045866 | 0.05343 | 2242 | 1.602 | 12 | 56/1 | 0.2001 | 52700 | 1.8836 | 20 | 2225 | 0.395 | 1 | 0
LAPWING/ACCC/TW | 0.051016 | 0.059868 | 1966 | 1.504 | 12 | 56/1 | 0.188 | 49000 | 1.6608 | 20 | 1960 | 0.385 | 1 | 0
BITTERN/ACCC/TW | 0.061477 | 0.072581 | 1572 | 1.345 | 12 | 39/1 | 0.2008 | 39300 | 1.3283 | 18 | 1554 | 0.345 | 1 | 0
CARDINAL/ACCC/TW | 0.077088 | 0.091894 | 1222 | 1.196 | 12 | 36/1 | 0.1843 | 37100 | 1.0536 | 16 | 1228 | 0.345 | 1 | 0
DRAKE/ACCC/TW | 0.090767 | 0.10863 | 1020 | 1.108 | 12 | 22/1 | 0.2154 | 41100 | 0.9116 | 14 | 1046 | 0.375 | 1 | 0
LINNET/ACCC/TW | 0.21115 | 0.25379 | 431 | 0.72 | 12 | 16/1 | 0.1641 | 16300 | 0.3819 | 10 | 439 | 0.235 | 1 | 0
DOVE/ACCC/TW | 0.12859 | 0.15418 | 713 | 0.927 | 12 | 18/1 | 0.199 | 27500 | 0.6328 | 11 | 727 | 0.305 | 1 | 0
GROSBEAK/ACCC/TW | 0.11265 | 0.13502 | 816 | 0.99 | 12 | 19/1 | 0.2072 | 30400 | 0.7215 | 12 | 832 | 0.32 | 1 | 0
6_0BusAlumTube | 0.0149 | 0.0175 | 999 | 6.625 | 13 | 99/0 | 0.1 | 99999 | 5.581 | 99 | 6564 | 9999 | 1 | 0
4_0BusAlumTube | 0.0261 | 0.0306 | 999 | 4.5 | 13 | 99/0 | 0.1 | 99999 | 3.174 | 99 | 3733 | 9999 | 1 | 0
1_0BusAlumTube | 0.1673 | 0.196 | 999 | 1.315 | 13 | 99/0 | 0.1 | 99999 | 0.4939 | 99 | 581 | 9999 | 1 | 0
1_5BusAlumTube | 0.1033 | 0.1211 | 999 | 1.9 | 13 | 99/0 | 0.1 | 99999 | 0.7995 | 99 | 940 | 9999 | 1 | 0
3_0BusAlumTube | 0.0372 | 0.0435 | 999 | 3.5 | 13 | 99/0 | 0.1 | 99999 | 2.228 | 99 | 2621 | 9999 | 1 | 0
2_5BusAlumTube | 0.0486 | 0.0569 | 999 | 2.875 | 13 | 99/0 | 0.1 | 99999 | 1.704 | 99 | 2004 | 9999 | 1 | 0
2_0BusAlumTube | 0.0769 | 0.0901 | 999 | 2.375 | 13 | 99/0 | 0.1 | 99999 | 1.075 | 99 | 1264 | 9999 | 1 | 0
3_5BusAlumTube | 0.0309 | 0.0362 | 999 | 4 | 13 | 99/0 | 0.1 | 99999 | 2.68 | 99 | 3151 | 9999 | 1 | 0
5_0BusAlumTube | 0.0193 | 0.0226 | 999 | 5.563 | 13 | 99/0 | 0.1 | 99999 | 4.3 | 99 | 5057 | 9999 | 1 | 0
2_5BusCuTube | 0.0246 | 0.0293 | 999 | 2.875 | 14 | 99/0 | 0.1 | 99999 | 1.583 | 99 | 6120 | 9999 | 1 | 0
3_0BusCuTube | 0.0206 | 0.0245 | 999 | 3.5 | 14 | 99/0 | 0.1 | 99999 | 2.257 | 99 | 8720 | 9999 | 1 | 0
3_5BusCuTube | 0.0186 | 0.0221 | 999 | 4 | 14 | 99/0 | 0.1 | 99999 | 2.945 | 99 | 11380 | 9999 | 1 | 0
2_0BusCuTube | 0.0424 | 0.0504 | 999 | 2.375 | 14 | 99/0 | 0.1 | 99999 | 1.091 | 99 | 4210 | 9999 | 1 | 0
1_5BusCuTube | 0.0578 | 0.0687 | 999 | 1.9 | 14 | 99/0 | 0.1 | 99999 | 0.8247 | 99 | 3190 | 9999 | 1 | 0
1_25BusCuTube | 0.0685 | 0.0815 | 999 | 1.66 | 14 | 99/0 | 0.1 | 99999 | 0.6944 | 99 | 2680 | 9999 | 1 | 0
1_0BusCuTube | 0.0866 | 0.1029 | 999 | 1.315 | 14 | 99/0 | 0.1 | 99999 | 0.4723 | 99 | 1830 | 9999 | 1 | 0
4_0BusCuTube | 0.0151 | 0.0179 | 999 | 4.5 | 14 | 99/0 | 0.1 | 99999 | 3.338 | 99 | 12900 | 9999 | 1 | 0
0_75BusCuTube | 0.1218 | 0.1449 | 999 | 1.05 | 14 | 99/0 | 0.1 | 99999 | 0.3352 | 99 | 1300 | 9999 | 1 | 0

## SWRate
Table from SWRate-v4.2 CondData.mdb
Name | CodeWord | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp | Low Resistance | Hi Temp | Hi Resistance | Al Weight | St Weight
AAAC | Akron | 30.58 | 7 |  | 0.0661 |  |  | 0.198 |  |  |  | 25 | 3.5394 | 75 | 4.1430 | 28.5
AAAC | Alliance | 246.9 | 7 |  | 0.1878 |  |  | 0.563 |  |  |  | 25 | 0.4391 | 75 | 0.5137 | 230.2
AAAC | Alton | 48.69 | 7 |  | 0.0834 |  |  | 0.250 |  |  |  | 25 | 2.2235 | 75 | 2.6026 | 45.4
AAAC | Amarillo | 246.9 | 19 |  | 0.1140 |  |  | 0.570 |  |  |  | 25 | 0.4391 | 75 | 0.5137 | 230.3
AAAC | Ames | 77.47 | 7 |  | 0.1052 |  |  | 0.316 |  |  |  | 25 | 1.3973 | 75 | 1.6355 | 72.2
AAAC | Amherst | 195.7 | 7 |  | 0.1672 |  |  | 0.502 |  |  |  | 25 | 0.5536 | 75 | 0.6478 | 182.5
AAAC | Anaheim | 155.4 | 7 |  | 0.1490 |  |  | 0.447 |  |  |  | 25 | 0.6969 | 75 | 0.8156 | 144.9
AAAC | Azusa | 123.3 | 7 |  | 0.1327 |  |  | 0.398 |  |  |  | 25 | 0.8782 | 75 | 1.0278 | 114.9
AAAC | Butte | 312.8 | 19 |  | 0.1283 |  |  | 0.642 |  |  |  | 25 | 0.3469 | 75 | 0.4058 | 291.6
AAAC | Cairo | 465.4 | 19 |  | 0.1565 |  |  | 0.783 |  |  |  | 25 | 0.2339 | 75 | 0.2733 | 433.9
AAAC | Canton | 394.5 | 19 |  | 0.1441 |  |  | 0.721 |  |  |  | 25 | 0.2755 | 75 | 0.3221 | 367.9
AAAC | Darien | 559.5 | 19 |  | 0.1716 |  |  | 0.858 |  |  |  | 25 | 0.1950 | 75 | 0.2278 | 521.7
AAAC | Elgin | 652.4 | 19 |  | 0.1853 |  |  | 0.927 |  |  |  | 25 | 0.1677 | 75 | 0.1958 | 608.3
AAAC | Flint | 740.8 | 37 |  | 0.1415 |  |  | 0.991 |  |  |  | 25 | 0.1482 | 75 | 0.1728 | 690.8
AAAC | Greeley | 927.2 | 37 |  | 0.1583 |  |  | 1.108 |  |  |  | 25 | 0.1193 | 75 | 0.1389 | 864.6
AAC | Anemone | 874.5 | 37 |  | 0.1538 |  |  | 1.077 |  |  |  | 25 | 0.1090 | 75 | 0.1298 | 820.3
AAC | Arbutus | 795 | 37 |  | 0.1466 |  |  | 1.026 |  |  |  | 25 | 0.1197 | 75 | 0.1425 | 745.3
AAC | Aster | 2/0 | 7 |  | 0.1379 |  |  | 0.414 |  |  |  | 25 | 0.7000 | 75 | 0.8384 | 124.8
AAC | Bluebell | 1033.5 | 37 |  | 0.1671 |  |  | 1.170 |  |  |  | 25 | 0.0934 | 75 | 0.1107 | 968.3
AAC | Bluebonnet | 3500 | 127 |  | 0.1660 |  |  | 2.158 |  |  |  | 25 | 0.0355 | 75 | 0.0399 | 3345
AAC | Cameilla | 1000 | 61 |  | 0.1280 |  |  | 1.152 |  |  |  | 25 | 0.0963 | 75 | 0.1142 | 936.8
AAC | Canna | 397.5 | 19 |  | 0.1447 |  |  | 0.724 |  |  |  | 25 | 0.2355 | 75 | 0.2817 | 372.9
AAC | Carnation | 1431 | 61 |  | 0.1532 |  |  | 1.379 |  |  |  | 25 | 0.0695 | 75 | 0.0817 | 1342
AAC | Cattail | 750 | 61 |  | 0.1109 |  |  | 0.998 |  |  |  | 25 | 0.1266 | 75 | 0.1508 | 703.2
AAC | Cockscomb | 900 | 37 |  | 0.156 |  |  | 1.092 |  |  |  | 25 | 0.1064 | 75 | 0.1264 | 844
AAC | Columbine | 1351.5 | 61 |  | 0.1488 |  |  | 1.340 |  |  |  | 25 | 0.0731 | 75 | 0.0861 | 1266
AAC | Coreopsis | 1590 | 61 |  | 0.1614 |  |  | 1.454 |  |  |  | 25 | 0.0635 | 75 | 0.0743 | 1489
AAC | Cosmos | 477 | 19 |  | 0.1584 |  |  | 0.793 |  |  |  | 25 | 0.1968 | 75 | 0.2352 | 446.8
AAC | Cowslip | 2000 | 91 |  | 0.1482 |  |  | 1.630 |  |  |  | 25 | 0.0525 | 75 | 0.0609 | 1873
AAC | Crocus | 874.5 | 61 |  | 0.1198 |  |  | 1.078 |  |  |  | 25 | 0.1090 | 75 | 0.1300 | 820.6
AAC | Daffodil | 350 | 19 |  | 0.1357 |  |  | 0.679 |  |  |  | 25 | 0.2672 | 75 | 0.3197 | 327.9
AAC | Dahlia | 556.5 | 19 |  | 0.1711 |  |  | 0.856 |  |  |  | 25 | 0.1691 | 75 | 0.2020 | 521.4
AAC | Daisy | 266.8 | 7 |  | 0.1953 |  |  | 0.586 |  |  |  | 25 | 0.3499 | 75 | 0.4188 | 250.2
AAC | Flag | 700 | 61 |  | 0.1071 |  |  | 0.964 |  |  |  | 25 | 0.1353 | 75 | 0.1613 | 655.8
AAC | Galdious | 1510.5 | 61 |  | 0.1574 |  |  | 1.417 |  |  |  | 25 | 0.0663 | 75 | 0.0778 | 1417
AAC | Goldenrod | 954 | 61 |  | 0.1251 |  |  | 1.126 |  |  |  | 25 | 0.1007 | 75 | 0.1195 | 894.8
AAC | Goldentuft | 450 | 19 |  | 0.1539 |  |  | 0.769 |  |  |  | 25 | 0.2084 | 75 | 0.2491 | 421.8
AAC | Hawkweed | 1000 | 37 |  | 0.1644 |  |  | 1.150 |  |  |  | 25 | 0.0963 | 75 | 0.1142 | 937.3
AAC | Hawthorn | 1192.5 | 61 |  | 0.1398 |  |  | 1.258 |  |  |  | 25 | 0.0819 | 75 | 0.0967 | 1117
AAC | Hyacinth | 500 | 37 |  | 0.1162 |  |  | 0.813 |  |  |  | 25 | 0.1879 | 75 | 0.2245 | 468.3
AAC | Iris | 2 | 7 |  | 0.0974 |  |  | 0.292 |  |  |  | 25 | 1.4031 | 75 | 1.6808 | 62.2
AAC | Jessamine | 1750 | 61 |  | 0.1694 |  |  | 1.525 |  |  |  | 25 | 0.0585 | 75 | 0.0683 | 1641
AAC | Larkspur | 1033.5 | 61 |  | 0.1302 |  |  | 1.172 |  |  |  | 25 | 0.0934 | 75 | 0.1107 | 969.2
AAC | Laurel | 266.8 | 19 |  | 0.1185 |  |  | 0.593 |  |  |  | 25 | 0.3499 | 75 | 0.4188 | 250.1
AAC | Lilac | 795 | 61 |  | 0.1142 |  |  | 1.028 |  |  |  | 25 | 0.1197 | 75 | 0.1425 | 745.7
AAC | Lupine | 2500 | 91 |  | 0.1657 |  |  | 1.823 |  |  |  | 25 | 0.0446 | 75 | 0.0511 | 2365
AAC | Magnolia | 954 | 37 |  | 0.1606 |  |  | 1.124 |  |  |  | 25 | 0.1007 | 75 | 0.1195 | 894.5
AAC | Marigold | 1113 | 61 |  | 0.1351 |  |  | 1.216 |  |  |  | 25 | 0.0872 | 75 | 0.1032 | 1044
AAC | Meadowsweet | 600 | 37 |  | 0.1273 |  |  | 0.891 |  |  |  | 25 | 0.1571 | 75 | 0.1875 | 562
AAC | Misteltoe | 556.5 | 37 |  | 0.1226 |  |  | 0.858 |  |  |  | 25 | 0.1691 | 75 | 0.2020 | 521.3
AAC | Narcissus | 1272 | 61 |  | 0.1444 |  |  | 1.300 |  |  |  | 25 | 0.0772 | 75 | 0.0912 | 1192
AAC | Nasturtium | 715.5 | 61 |  | 0.1083 |  |  | 0.975 |  |  |  | 25 | 0.1325 | 75 | 0.1578 | 670.6
AAC | Orchid | 636 | 37 |  | 0.1311 |  |  | 0.918 |  |  |  | 25 | 0.1485 | 75 | 0.1771 | 596.1
AAC | Oxlip | 4/0 | 7 |  | 0.1739 |  |  | 0.522 |  |  |  | 25 | 0.4407 | 75 | 0.5277 | 198.4
AAC | Pansy | 1 | 7 |  | 0.1093 |  |  | 0.328 |  |  |  | 25 | 1.1128 | 75 | 1.3330 | 78.4
AAC | Peachbell | 6 | 7 |  | 0.0612 |  |  | 0.184 |  |  |  | 25 | 3.5471 | 75 | 4.2493 | 24.6
AAC | Peony | 300 | 19 |  | 0.1257 |  |  | 0.629 |  |  |  | 25 | 0.3113 | 75 | 0.3726 | 281.4
AAC | Petunia | 750 | 37 |  | 0.1424 |  |  | 0.997 |  |  |  | 25 | 0.1266 | 75 | 0.1508 | 703.2
AAC | Phlox | 3/0 | 7 |  | 0.1548 |  |  | 0.464 |  |  |  | 25 | 0.5543 | 75 | 0.6652 | 157.2
AAC | Poppy | 1/0 | 7 |  | 0.1228 |  |  | 0.368 |  |  |  | 25 | 0.8829 | 75 | 1.0576 | 98.9
AAC | Rose | 4 | 7 |  | 0.0772 |  |  | 0.232 |  |  |  | 25 | 2.2308 | 75 | 2.6725 | 39.1
AAC | Snapdragon | 900 | 61 |  | 0.1215 |  |  | 1.094 |  |  |  | 25 | 0.1064 | 75 | 0.1264 | 844
AAC | Sneezewort | 250 | 7 |  | 0.1890 |  |  | 0.567 |  |  |  | 25 | 0.3733 | 75 | 0.4469 | 234.4
AAC | Syringa | 477 | 37 |  | 0.1135 |  |  | 0.795 |  |  |  | 25 | 0.1968 | 75 | 0.2352 | 446.8
AAC | Trilium | 3000 | 127 |  | 0.1537 |  |  | 1.996 |  |  |  | 25 | 0.0392 | 75 | 0.0445 | 2840
AAC | Tulip | 336.4 | 19 |  | 0.1331 |  |  | 0.666 |  |  |  | 25 | 0.2779 | 75 | 0.3325 | 315.5
AAC | Valerian | 250 | 19 |  | 0.1147 |  |  | 0.574 |  |  |  | 25 | 0.3733 | 75 | 0.4469 | 234.3
AAC | Verbena | 700 | 37 |  | 0.1375 |  |  | 0.963 |  |  |  | 25 | 0.1353 | 75 | 0.1613 | 655.7
AAC | Violet | 715.5 | 37 |  | 0.1391 |  |  | 0.974 |  |  |  | 25 | 0.1325 | 75 | 0.1578 | 671
AAC | Zinnia | 500 | 19 |  | 0.1622 |  |  | 0.811 |  |  |  | 25 | 0.1879 | 75 | 0.2245 | 468.5
AACSR | 1033.5 - 45/7 | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.1062 | 75 | 0.1244 | 967.8 | 189.8
AACSR | 1033.5 - 54/7 | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.246 |  |  |  | 25 | 0.1049 | 75 | 0.1254 | 967.8 | 356
AACSR | 1113.0 - 45/7 | 1113.0 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.259 |  |  |  | 25 | 0.0990 | 75 | 0.1158 | 1043.4 | 204.8
AACSR | 1113.0 - 54/19 | 1113.0 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.293 |  |  |  | 25 | 0.0981 | 75 | 0.1172 | 1048.5 | 376.1
AACSR | 1192.5 - 45/7 | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0927 | 75 | 0.1083 | 1117.6 | 219.1
AACSR | 1192.5 - 54/19 | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.338 |  |  |  | 25 | 0.0918 | 75 | 0.1096 | 1122.8 | 402.7
AACSR | 1272.0 - 45/7 | 1272.0 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0872 | 75 | 0.1018 | 1191.6 | 233.9
AACSR | 1272.0 - 54/19 | 1272.0 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.382 |  |  |  | 25 | 0.0864 | 75 | 0.1029 | 1198.1 | 429.3
AACSR | 1351.5 - 45/7 | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0824 | 75 | 0.0961 | 1266.4 | 248.3
AACSR | 1351.5 - 54/19 | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0815 | 75 | 0.0970 | 1272.6 | 455.8
AACSR | 1431.0 - 45/7 | 1431.0 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0781 | 75 | 0.0910 | 1340.5 | 263.1
AACSR | 1431.0 - 54/19 | 1431.0 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0772 | 75 | 0.0918 | 1347.7 | 483.1
AACSR | 1510.5 - 45/7 | 1510.5 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0743 | 75 | 0.0864 | 1415.2 | 277.4
AACSR | 1510.5 - 54/19 | 1510.5 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0734 | 75 | 0.0872 | 1421.5 | 509.2
AACSR | 1590.0 - 45/7 | 1590.0 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.0709 | 75 | 0.0824 | 1490.4 | 292.2
AACSR | 1590.0 - 54/19 | 1590.0 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.545 |  |  |  | 25 | 0.0700 | 75 | 0.0830 | 1497.3 | 537
AACSR | 1780.0 - 84/19 | 1780.0 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.602 |  |  |  | 25 | 0.0640 | 75 | 0.0739 | 1676.8 | 386.6
AACSR | 2034.5 - 72/7 | 2034.5 | 72 | 7 | 0.1681 | 0.1122 | 0.3366 | 1.681 |  |  |  | 25 | 0.0577 | 75 | 0.0663 | 1915.8 | 234.3
AACSR | 2057.0 - 76/19 | 2057.0 | 76 | 19 | 0.1645 | 0.0768 | 0.384 | 1.7 |  |  |  | 25 | 0.0569 | 75 | 0.0653 | 1936.5 | 298.5
AACSR | 2156.0 - 84/19 | 2156.0 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0541 | 75 | 0.0621 | 2029.9 | 467.4
AACSR | 2167.0 - 72/7 | 2167.0 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0547 | 75 | 0.0627 | 2040.8 | 249.1
AACSR | 2312.0 - 76/19 | 2312.0 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0516 | 75 | 0.0589 | 2176.6 | 335.4
AACSR | 2515.0 - 76/19 | 2515.0 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.88 |  |  |  | 25 | 0.0481 | 75 | 0.0548 | 2367.9 | 364.8
AACSR | 266.8 - 26/7 | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.3980 | 75 | 0.4656 | 250 | 115.6
AACSR | 266.8 - 30/7 | 266.8 | 30 | 7 | 0.0943 | 0.0943 | 0.2829 | 0.66 |  |  |  | 25 | 0.3946 | 75 | 0.4616 | 250.6 | 165.5
AACSR | 300.0 - 26/7 | 300.0 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.68 |  |  |  | 25 | 0.3540 | 75 | 0.4142 | 281 | 129.8
AACSR | 336.4 - 26/7 | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.72 |  |  |  | 25 | 0.3158 | 75 | 0.3694 | 315 | 145.4
AACSR | 336.4 - 30/7 | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.3131 | 75 | 0.3663 | 316 | 208.7
AACSR | 397.5 - 26/7 | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2675 | 75 | 0.3128 | 372.2 | 171.9
AACSR | 397.5 - 30/7 | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2651 | 75 | 0.3101 | 373.3 | 246.5
AACSR | 477.0 - 26/7 | 477.0 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.2231 | 75 | 0.2608 | 446.7 | 206.4
AACSR | 477.0 - 30/7 | 477.0 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.2211 | 75 | 0.2586 | 448.1 | 295.9
AACSR | 556.5 - 26/7 | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1915 | 75 | 0.2238 | 521.5 | 241
AACSR | 556.5 - 30/7 | 556.5 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 0.953 |  |  |  | 25 | 0.1897 | 75 | 0.2218 | 522.8 | 345.2
AACSR | 605.0 - 26/7 | 605.0 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1763 | 75 | 0.2060 | 566.6 | 261.8
AACSR | 605.0 - 30/19 | 605.0 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1748 | 75 | 0.2043 | 568.2 | 367.4
AACSR | 605.0 - 30/7 | 605.0 | 30 | 7 | 0.142 | 0.142 | 0.426 | 0.994 |  |  |  | 25 | 0.1746 | 75 | 0.2041 | 568.2 | 375.3
AACSR | 636.0 - 26/7 | 636.0 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.99 |  |  |  | 25 | 0.1678 | 75 | 0.1960 | 596 | 275.2
AACSR | 636.0 - 30/19 | 636.0 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1663 | 75 | 0.1944 | 597.4 | 386.6
AACSR | 636.0 - 30/7 | 636.0 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.019 |  |  |  | 25 | 0.1662 | 75 | 0.1942 | 597.4 | 394.5
AACSR | 666.6 - 26/7 | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1601 | 75 | 0.1871 | 624.5 | 288.5
AACSR | 715.5 - 26/7 | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1493 | 75 | 0.1744 | 670.6 | 309.7
AACSR | 715.5 - 30/19 | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1481 | 75 | 0.1730 | 671.8 | 434
AACSR | 795.0 - 26/7 | 795.0 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.1346 | 75 | 0.1572 | 745.3 | 344.2
AACSR | 795.0 - 30/19 | 795.0 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.14 |  |  |  | 25 | 0.1334 | 75 | 0.1558 | 746.9 | 483.1
AACSR | 795.0 - 45/7 | 795.0 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1670 | 75 | 0.1609 | 744.8 | 146.1
AACSR | 795.0 - 54/7 | 795.0 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1354 | 75 | 0.1625 | 744.5 | 273.8
AACSR | 795.0 - 30/7 | 795.0 | 30 | 7 | 0.1628 | 0.1628 | 0.4884 | 1.14 |  |  |  | 25 | 0.1333 | 75 | 0.1557 | 746.9 | 493.2
AACSR | 900.0 - 45/7 | 900.0 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1214 | 75 | 0.1424 | 843.1 | 165.5
AACSR | 900.0 - 54/7 | 900.0 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.1200 | 75 | 0.1437 | 843.4 | 310.2
AACSR | 954.0 - 45/7 | 954.0 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.1148 | 75 | 0.1345 | 893.9 | 175.5
AACSR | 954.0 - 54/7 | 954.0 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.1133 | 75 | 0.1357 | 893.7 | 328.7
AACSR | 954.0 - 30/19 | 954.0 | 30 | 19 | 0.1783 | 0.107 | 0.535 | 1.248 |  |  |  | 25 | 0.1116 | 75 | 0.1302 | 895.9 | 579.5
AACTW | Arbutus/TW | 795 | 17 |  |  |  |  | 0.919 |  |  | 2 | 25 | 0.1197 | 75 | 0.1425 | 745.1
AACTW | Baker/TW | 1346.8 | 31 |  |  |  |  | 1.2 |  |  | 3 | 25 | 0.0734 | 75 | 0.0864 | 1262.3
AACTW | Bluebell/TW | 1033.5 | 31 |  |  |  |  | 1.057 |  |  | 3 | 25 | 0.0934 | 75 | 0.1107 | 968.7
AACTW | Canna/TW | 397.5 | 17 |  |  |  |  | 0.661 |  |  | 2 | 25 | 0.2355 | 75 | 0.2817 | 372.6
AACTW | Carnation/TW | 1431 | 31 |  |  |  |  | 1.236 |  |  | 3 | 25 | 0.0695 | 75 | 0.0817 | 1341.3
AACTW | Cockscomb/TW | 900 | 17 |  |  |  |  | 0.99 |  |  | 3 | 25 | 0.1064 | 75 | 0.1264 | 843.6
AACTW | Columbine/TW | 1351.5 | 31 |  |  |  |  | 1.202 |  |  | 3 | 25 | 0.0731 | 75 | 0.0861 | 1266.3
AACTW | Coreopsis/TW | 1590 | 49 |  |  |  |  | 1.315 |  |  | 4 | 25 | 0.0635 | 75 | 0.0743 | 1490.3
AACTW | Cosmos/TW | 477 | 17 |  |  |  |  | 0.72 |  |  | 2 | 25 | 0.1968 | 75 | 0.2352 | 447.1
AACTW | Cowslip/TW | 2000 | 49 |  |  |  |  | 1.468 |  |  | 4 | 25 | 0.0525 | 75 | 0.0609 | 1893.0
AACTW | Hawkweed/TW | 1000 | 31 |  |  |  |  | 1.041 |  |  | 3 | 25 | 0.0963 | 75 | 0.1142 | 937.3
AACTW | Hawthorn/TW | 1192.5 | 31 |  |  |  |  | 1.132 |  |  | 3 | 25 | 0.0819 | 75 | 0.0967 | 1117.7
AACTW | Helens/TW | 1123.1 | 31 |  |  |  |  | 1.1 |  |  | 3 | 25 | 0.0865 | 75 | 0.1023 | 1052.7
AACTW | Hood/TW | 1583.2 | 34 |  |  |  |  | 1.3 |  |  | 3 | 25 | 0.0637 | 75 | 0.0746 | 1483.9
AACTW | Jefferson/TW | 2388.1 | 52 |  |  |  |  | 1.6 |  |  | 4 | 25 | 0.0461 | 75 | 0.0530 | 2260.3
AACTW | Jessamine/TW | 1750 | 49 |  |  |  |  | 1.377 |  |  | 4 | 25 | 0.0585 | 75 | 0.0683 | 1640.3
AACTW | Logan/TW | 322.5 | 17 |  |  |  |  | 0.6 |  |  | 2 | 25 | 0.2898 | 75 | 0.3468 | 302.3
AACTW | Lupine/TW | 2500 | 71 |  |  |  |  | 1.648 |  |  | 5 | 25 | 0.0446 | 75 | 0.0511 | 2366.2
AACTW | Magnolia/TW | 954 | 31 |  |  |  |  | 1.018 |  |  | 3 | 25 | 0.1007 | 75 | 0.1195 | 894.2
AACTW | Marigold/TW | 1113 | 31 |  |  |  |  | 1.095 |  |  | 3 | 25 | 0.0872 | 75 | 0.1032 | 1043.2
AACTW | McKinley/TW | 761.5 | 17 |  |  |  |  | 0.9 |  |  | 2 | 25 | 0.1247 | 75 | 0.1486 | 713.7
AACTW | Meadowsweet/TW | 600 | 17 |  |  |  |  | 0.803 |  |  | 2 | 25 | 0.1571 | 75 | 0.1875 | 562.4
AACTW | Mistletoe/TW | 556.5 | 17 |  |  |  |  | 0.775 |  |  | 2 | 25 | 0.1691 | 75 | 0.2020 | 521.3
AACTW | Narcissus/TW | 1272 | 31 |  |  |  |  | 1.168 |  |  | 3 | 25 | 0.0772 | 75 | 0.0911 | 1192.2
AACTW | Nasturtium/TW | 750 | 17 |  |  |  |  | 0.893 |  |  | 2 | 25 | 0.1266 | 75 | 0.1508 | 702.1
AACTW | Orchid/TW | 636 | 17 |  |  |  |  | 0.825 |  |  | 2 | 25 | 0.1485 | 75 | 0.1771 | 596.1
AACTW | Powell/TW | 2093.6 | 49 |  |  |  |  | 1.5 |  |  | 4 | 25 | 0.0510 | 75 | 0.0591 | 1981.6
AACTW | Rainier/TW | 918.8 | 31 |  |  |  |  | 1.000 |  |  | 3 | 25 | 0.1043 | 75 | 0.1239 | 861.2
AACTW | Robson/TW | 595.8 | 17 |  |  |  |  | 0.8 |  |  | 2 | 25 | 0.1582 | 75 | 0.1888 | 558.4
AACTW | Trillium/TW | 3000 | 71 |  |  |  |  | 1.799 |  |  | 5 | 25 | 0.0392 | 75 | 0.0445 | 2839.5
AACTW | Tulip/TW | 336.4 | 17 |  |  |  |  | 0.612 |  |  | 2 | 25 | 0.2779 | 75 | 0.3325 | 315.3
AACTW | Verbena/TW | 700 | 17 |  |  |  |  | 0.864 |  |  | 2 | 25 | 0.1353 | 75 | 0.1613 | 656.1
AACTW | Wheeler/TW | 449.4 | 17 |  |  |  |  | 0.7 |  |  | 2 | 25 | 0.2087 | 75 | 0.2494 | 421.2
AACTW | Whitney/TW | 1812.7 | 49 |  |  |  |  | 1.4 |  |  | 4 | 25 | 0.0568 | 75 | 0.0662 | 1699.0
AACTW | Zinnia/TW | 500 | 17 |  |  |  |  | 0.736 |  |  | 2 | 25 | 0.1879 | 75 | 0.2245 | 468.7
ACAR | 1024.5 - 18/19 | 1024.5 | 18 | 19 | 0.1664 | 0.1664 | 1.23 | 1.165 |  |  |  | 25 | 0.1010 | 75 | 0.1187 | 957.7
ACAR | 1024.5 - 30/7 | 1024.5 | 30 | 7 | 0.1664 | 0.1664 | 0.272 | 1.165 |  |  |  | 25 | 0.0966 | 75 | 0.1142 | 959.3
ACAR | 1024.5 - 24/13 | 1024.5 | 24 | 13 | 0.1664 | 0.1664 | 0.631 | 1.165 |  |  |  | 25 | 0.0987 | 75 | 0.1164 | 958.5
ACAR | 1081 - 18/19 | 1081 | 18 | 19 | 0.1709 | 0.1709 | 1.262 | 1.196 |  |  |  | 25 | 0.0960 | 75 | 0.1127 | 1010.2
ACAR | 1081 - 30/7 | 1081 | 30 | 7 | 0.1709 | 0.1709 | 0.279 | 1.196 |  |  |  | 25 | 0.0918 | 75 | 0.1084 | 1011.9
ACAR | 1081 - 24/13 | 1081 | 24 | 13 | 0.1709 | 0.1709 | 0.648 | 1.196 |  |  |  | 25 | 0.0939 | 75 | 0.1105 | 1011.1
ACAR | 1109 - 18/19 | 1109 | 18 | 19 | 0.1731 | 0.1731 | 1.279 | 1.212 |  |  |  | 25 | 0.0937 | 75 | 0.1100 | 1036.4
ACAR | 1109 - 30/7 | 1109 | 30 | 7 | 0.1731 | 0.1731 | 0.283 | 1.212 |  |  |  | 25 | 0.0897 | 75 | 0.1058 | 1038.1
ACAR | 1109 - 24/13 | 1109 | 24 | 13 | 0.1731 | 0.1731 | 0.657 | 1.212 |  |  |  | 25 | 0.0917 | 75 | 0.1078 | 1037.2
ACAR | 1172 - 18/19 | 1172 | 18 | 19 | 0.178 | 0.178 | 1.315 | 1.246 |  |  |  | 25 | 0.0891 | 75 | 0.1044 | 1095.9
ACAR | 1172 - 30/7 | 1172 | 30 | 7 | 0.178 | 0.178 | 0.291 | 1.246 |  |  |  | 25 | 0.0852 | 75 | 0.1004 | 1097.7
ACAR | 1172 - 24/13 | 1172 | 24 | 13 | 0.178 | 0.178 | 0.675 | 1.246 |  |  |  | 25 | 0.0871 | 75 | 0.1024 | 1096.8
ACAR | 1172 - 33/4 | 1172 | 33 | 4 | 0.1780 | 0.1780 | 0.151 | 1.246 |  |  |  | 25 | 0.0843 | 75 | 0.0995 | 1098.2
ACAR | 1197 - 18/19 | 1197 | 18 | 19 | 0.1799 | 0.1799 | 1.329 | 1.259 |  |  |  | 25 | 0.0873 | 75 | 0.1023 | 1119.4
ACAR | 1197 - 30/7 | 1197 | 30 | 7 | 0.1799 | 0.1799 | 0.294 | 1.259 |  |  |  | 25 | 0.0836 | 75 | 0.0985 | 1121.3
ACAR | 1197 - 24/13 | 1197 | 24 | 13 | 0.1799 | 0.1799 | 0.682 | 1.259 |  |  |  | 25 | 0.0854 | 75 | 0.1003 | 1120.3
ACAR | 1280 - 18/19 | 1280 | 18 | 19 | 0.186 | 0.186 | 1.374 | 1.302 |  |  |  | 25 | 0.0821 | 75 | 0.0961 | 1196.6
ACAR | 1280 - 30/7 | 1280 | 30 | 7 | 0.186 | 0.186 | 0.304 | 1.302 |  |  |  | 25 | 0.0787 | 75 | 0.0925 | 1198.6
ACAR | 1280 - 24/13 | 1280 | 24 | 13 | 0.186 | 0.186 | 0.705 | 1.302 |  |  |  | 25 | 0.0803 | 75 | 0.0942 | 1197.6
ACAR | 1362 - 42/19 | 1362 | 42 | 19 | 0.1494 | 0.1494 | 0.608 | 1.345 |  |  |  | 25 | 0.0756 | 75 | 0.0886 | 1274.1
ACAR | 1362 - 54/7 | 1362 | 54 | 7 | 0.1494 | 0.1494 | 0.174 | 1.345 |  |  |  | 25 | 0.0737 | 75 | 0.0888 | 1275.4
ACAR | 1703 - 42/19 | 1703 | 42 | 19 | 0.1671 | 0.1671 | 0.68 | 1.504 |  |  |  | 25 | 0.0622 | 75 | 0.0723 | 1593.9
ACAR | 1703 - 48/13 | 1703 | 48 | 13 | 0.1671 | 0.1671 | 0.407 | 1.504 |  |  |  | 25 | 0.0614 | 75 | 0.0715 | 1594.7
ACAR | 1703 - 54/7 | 1703 | 54 | 7 | 0.1671 | 0.1671 | 0.195 | 1.504 |  |  |  | 25 | 0.0607 | 75 | 0.0725 | 1595.5
ACAR | 1933 - 42/19 | 1933 | 42 | 19 | 0.1780 | 0.1780 | 0.725 | 1.602 |  |  |  | 25 | 0.0559 | 75 | 0.0647 | 1808.6
ACAR | 1933 - 48/13 | 1933 | 48 | 13 | 0.178 | 0.178 | 0.434 | 1.602 |  |  |  | 25 | 0.0553 | 75 | 0.0641 | 1809.5
ACAR | 1933 - 54/7 | 1933 | 54 | 7 | 0.178 | 0.178 | 0.208 | 1.602 |  |  |  | 25 | 0.0546 | 75 | 0.0648 | 1810.4
ACAR | 2267 - 42/19 | 2267 | 42 | 19 | 0.1928 | 0.1928 | 0.785 | 1.735 |  |  |  | 25 | 0.0496 | 75 | 0.0571 | 2142.7
ACAR | 2267 - 48/13 | 2267 | 48 | 13 | 0.1928 | 0.1928 | 0.47 | 1.735 |  |  |  | 25 | 0.0491 | 75 | 0.0565 | 2143.8
ACAR | 2267 - 54/7 | 2267 | 54 | 7 | 0.1928 | 0.1928 | 0.225 | 1.735 |  |  |  | 25 | 0.0486 | 75 | 0.0571 | 2144.9
ACAR | 2338 - 42/19 | 2338 | 42 | 19 | 0.1958 | 0.1958 | 0.797 | 1.762 |  |  |  | 25 | 0.0484 | 75 | 0.0556 | 2209.9
ACAR | 2338 - 48/13 | 2338 | 48 | 13 | 0.1958 | 0.1958 | 0.477 | 1.762 |  |  |  | 25 | 0.0479 | 75 | 0.0551 | 2211
ACAR | 2338 - 54/7 | 2338 | 54 | 7 | 0.1958 | 0.1958 | 0.228 | 1.762 |  |  |  | 25 | 0.0474 | 75 | 0.0557 | 2212.1
ACAR | 355 - 12/7 | 355 | 12 | 7 | 0.1367 | 0.1367 | 0.399 | 0.684 |  |  |  | 25 | 0.2776 | 75 | 0.3296 | 333
ACAR | 355 - 15/4 | 355 | 15 | 4 | 0.1367 | 0.1367 | 0.182 | 0.684 |  |  |  | 25 | 0.2714 | 75 | 0.3233 | 333.3
ACAR | 395.1 - 15/4 | 395.1 | 15 | 4 | 0.1442 | 0.1442 | 0.192 | 0.721 |  |  |  | 25 | 0.2441 | 75 | 0.2907 | 369.9
ACAR | 465.9 - 12/7 | 465.9 | 12 | 7 | 0.1566 | 0.1566 | 0.457 | 0.783 |  |  |  | 25 | 0.2121 | 75 | 0.2517 | 435.9
ACAR | 503.6 - 12/7 | 503.6 | 12 | 7 | 0.1628 | 0.1628 | 0.475 | 0.814 |  |  |  | 25 | 0.1965 | 75 | 0.2330 | 471.1
ACAR | 503.6 - 15/4 | 503.6 | 15 | 4 | 0.1628 | 0.1628 | 0.217 | 0.814 |  |  |  | 25 | 0.1921 | 75 | 0.2286 | 471.5
ACAR | 559.5 - 15/4 | 559.5 | 15 | 4 | 0.1716 | 0.1716 | 0.229 | 0.858 |  |  |  | 25 | 0.1732 | 75 | 0.2060 | 523.8
ACAR | 587.2 - 15/4 | 587.2 | 15 | 4 | 0.1758 | 0.1758 | 0.234 | 0.879 |  |  |  | 25 | 0.1652 | 75 | 0.1964 | 549.8
ACAR | 653.1 - 12/7 | 653.1 | 12 | 7 | 0.1854 | 0.1854 | 0.541 | 0.927 |  |  |  | 25 | 0.1523 | 75 | 0.1804 | 611
ACAR | 653.1 - 15/4 | 653.1 | 15 | 4 | 0.1854 | 0.1854 | 0.247 | 0.927 |  |  |  | 25 | 0.1490 | 75 | 0.1769 | 611.5
ACAR | 739.8 - 18/19 | 739.8 | 18 | 19 | 0.1414 | 0.1414 | 1.045 | 0.99 |  |  |  | 25 | 0.1378 | 75 | 0.1625 | 691.6
ACAR | 739.8 - 30/7 | 739.8 | 30 | 7 | 0.1414 | 0.1414 | 0.231 | 0.99 |  |  |  | 25 | 0.1316 | 75 | 0.1562 | 692.7
ACAR | 739.8 - 24/13 | 739.8 | 24 | 13 | 0.1414 | 0.1414 | 0.536 | 0.99 |  |  |  | 25 | 0.1346 | 75 | 0.1593 | 692.1
ACAR | 739.8 - 33/4 | 739.8 | 33 | 4 | 0.1414 | 0.1414 | 0.12 | 0.99 |  |  |  | 25 | 0.1302 | 75 | 0.1547 | 693
ACAR | 853.7 - 18/19 | 853.7 | 18 | 19 | 0.1519 | 0.1519 | 1.122 | 1.063 |  |  |  | 25 | 0.1201 | 75 | 0.1414 | 798.1
ACAR | 853.7 - 30/7 | 853.7 | 30 | 7 | 0.1519 | 0.1519 | 0.248 | 1.063 |  |  |  | 25 | 0.1147 | 75 | 0.1359 | 799.4
ACAR | 853.7 - 24/13 | 853.7 | 24 | 13 | 0.1519 | 0.1519 | 0.576 | 1.063 |  |  |  | 25 | 0.1173 | 75 | 0.1386 | 798.7
ACAR | 927.2 - 18/19 | 927.2 | 18 | 19 | 0.1583 | 0.1583 | 1.17 | 1.108 |  |  |  | 25 | 0.1110 | 75 | 0.1305 | 866.7
ACAR | 927.2 - 30/7 | 927.2 | 30 | 7 | 0.1583 | 0.1583 | 0.259 | 1.108 |  |  |  | 25 | 0.1061 | 75 | 0.1255 | 868.2
ACAR | 927.2 - 24/13 | 927.2 | 24 | 13 | 0.1583 | 0.1583 | 0.6 | 1.108 |  |  |  | 25 | 0.1084 | 75 | 0.1280 | 867.5
ACCR | 1851-T13 | 1851 | 54 | 19 | 0.185 | 0.111 | 0.556 | 1.667 |  | 13 | 3 | 25 | 0.0523 | 75 | 0.0615 | 1752.4 | 272.8
ACCR | 195-T20 | 195 | 7 | 7 | 0.167 | 0.074 | 0.222 | 0.556 |  | 20 | 1 | 25 | 0.4513 | 75 | 0.5405 | 183.3 | 45.7
ACCR | 207-T23 | 207 | 30 | 7 | 0.083 | 0.083 | 0.249 | 0.582 |  | 23 | 2 | 25 | 0.4187 | 75 | 0.5015 | 195.6 | 57.2
ACCR | 427-T13 | 427 | 24 | 7 | 0.133 | 0.089 | 0.267 | 0.8 |  | 13 | 2 | 25 | 0.2123 | 75 | 0.254 | 402 | 65.3
ACCR | 680-T19 | 680 | 28 | 19 | 0.156 | 0.083 | 0.416 | 1.039 |  | 19 | 2 | 25 | 0.1307 | 75 | 0.1561 | 641.8 | 153.4
ACCR | 951-T10 | 951 | 22 | 7 | 0.208 | 0.116 | 0.347 | 1.178 |  | 10 | 2 | 25 | 0.0981 | 75 | 0.1168 | 895.6 | 109.5
ACCR | Bittern | 1238 | 51 | 19 | 0.156 | 0.083 | 0.416 | 1.35 |  | 11 | 3 | 25 | 0.0764 | 75 | 0.0906 | 1179.9 | 153.4
ACCR | Brant | 373 | 24 | 7 | 0.125 | 0.083 | 0.249 | 0.748 |  | 13 | 2 | 25 | 0.2427 | 75 | 0.2905 | 351.2 | 57.2
ACCR | Condor | 795 | 24 | 19 | 0.185 | 0.074 | 0.371 | 1.112 |  | 13 | 2 | 25 | 0.1112 | 75 | 0.1327 | 775.8 | 122.3
ACCR | Curlew | 1036 | 54 | 19 | 0.139 | 0.083 | 0.416 | 1.247 |  | 13 | 3 | 25 | 0.0895 | 75 | 0.1066 | 980.4 | 153.4
ACCR | Dove | 573 | 26 | 7 | 0.149 | 0.116 | 0.347 | 0.941 |  | 16 | 2 | 25 | 0.1562 | 75 | 0.1868 | 540 | 109.5
ACCR | Drake | 824 | 26 | 19 | 0.178 | 0.083 | 0.416 | 1.128 |  | 16 | 2 | 25 | 0.1095 | 75 | 0.1307 | 776.5 | 153.4
ACCR | Eagle | 575 | 30 | 19 | 0.139 | 0.083 | 0.416 | 0.97 |  | 23 | 2 | 25 | 0.1517 | 75 | 0.1815 | 543.3 | 153.4
ACCR | Falcon | 1641 | 54 | 19 | 0.174 | 0.105 | 0.523 | 1.569 |  | 13 | 3 | 25 | 0.0583 | 75 | 0.0688 | 1553.3 | 242.1
ACCR | Flicker | 480 | 24 | 7 | 0.141 | 0.094 | 0.283 | 0.849 |  | 13 | 2 | 25 | 0.1888 | 75 | 0.2259 | 452.3 | 73.4
ACCR | Goldfinch | 634 | 22 | 7 | 0.17 | 0.094 | 0.283 | 0.962 |  | 10 | 2 | 25 | 0.1456 | 75 | 0.174 | 597 | 73.4
ACCR | Grosbeak | 656 | 26 | 19 | 0.159 | 0.074 | 0.371 | 1.006 |  | 16 | 2 | 25 | 0.1371 | 75 | 0.1638 | 617.4 | 122.3
ACCR | Hawk | 470 | 26 | 7 | 0.134 | 0.105 | 0.314 | 0.852 |  | 16 | 2 | 25 | 0.1901 | 75 | 0.2274 | 442.9 | 90.1
ACCR | Ibis | 382 | 26 | 7 | 0.121 | 0.094 | 0.283 | 0.768 |  | 16 | 2 | 25 | 0.2335 | 75 | 0.2796 | 360 | 73.4
ACCR | Junco | 267 | 30 | 7 | 0.094 | 0.094 | 0.283 | 0.66 |  | 23 | 2 | 25 | 0.3253 | 75 | 0.3896 | 251.8 | 73.4
ACCR | Lapwing | 1594 | 51 | 19 | 0.177 | 0.094 | 0.472 | 1.532 |  | 11 | 3 | 25 | 0.0605 | 75 | 0.0714 | 1509.1 | 197.1
ACCR | Lark | 400 | 30 | 7 | 0.116 | 0.116 | 0.347 | 0.809 |  | 23 | 2 | 25 | 0.2171 | 75 | 0.2599 | 377.9 | 109.5
ACCR | Linnet | 340 | 26 | 7 | 0.114 | 0.089 | 0.267 | 0.724 |  | 16 | 2 | 25 | 0.2626 | 75 | 0.3144 | 319.8 | 65.3
ACCR | Martin | 1334 | 54 | 19 | 0.157 | 0.094 | 0.472 | 1.415 |  | 13 | 3 | 25 | 0.0705 | 75 | 0.0836 | 1262.5 | 197.1
ACCR | Ostrich | 297 | 26 | 7 | 0.107 | 0.083 | 0.249 | 0.677 |  | 16 | 2 | 25 | 0.3004 | 75 | 0.3597 | 279.5 | 57.2
ACCR | Partridge | 257 | 26 | 7 | 0.1 | 0.077 | 0.232 | 0.63 |  | 16 | 2 | 25 | 0.3468 | 75 | 0.4145 | 242.5 | 49.8
ACCR | Peacock | 591 | 24 | 7 | 0.157 | 0.105 | 0.314 | 0.941 |  | 13 | 2 | 25 | 0.1539 | 75 | 0.1839 | 556.5 | 90.1
ACCR | Puffin | 780 | 22 | 7 | 0.188 | 0.105 | 0.314 | 1.067 |  | 10 | 2 | 25 | 0.1189 | 75 | 0.1418 | 734.6 | 90.1
ACCR | Stilt | 720 | 24 | 7 | 0.173 | 0.116 | 0.347 | 1.04 |  | 13 | 2 | 25 | 0.1266 | 75 | 0.1512 | 678.5 | 109.5
ACCRTW | 1033-T23/TW | 1033 | 24 | 19 | 0.2075 | 0.111 | 0.556 | 1.189 |  | 23 | 2 | 25 | 0.085 | 75 | 0.1013 | 969.4 | 273.8
ACCRTW | Calumet/TW | 565 | 20 | 7 | 0.1681 | 0.116 | 0.347 | 0.861 |  | 17 | 2 | 25 | 0.1578 | 75 | 0.1888 | 530.2 | 109.9
ACCRTW | Condor/TW | 795 | 20 | 19 | 0.1994 | 0.0741 | 0.371 | 0.995 |  | 13 | 2 | 25 | 0.1145 | 75 | 0.1367 | 746 | 122.7
ACCRTW | Cumberland/TW | 1927 | 42 | 19 | 0.2142 | 0.116 | 0.578 | 1.551 |  | 13 | 3 | 25 | 0.0499 | 75 | 0.0587 | 1818.9 | 295.7
ACCRTW | Curlew/TW | 1033 | 20 | 19 | 0.2273 | 0.083 | 0.416 | 1.132 |  | 13 | 2 | 25 | 0.0889 | 75 | 0.1059 | 969.4 | 153.9
ACCRTW | Hawk/TW | 477 | 18 | 7 | 0.163 | 0.105 | 0.314 | 0.789 |  | 16 | 2 | 25 | 0.187 | 75 | 0.2238 | 447.6 | 90.4
ACCRTW | Hudson/TW | 1158 | 22 | 19 | 0.229 | 0.089 | 0.445 | 1.199 |  | 13 | 2 | 25 | 0.0796 | 75 | 0.0947 | 1086.7 | 175.9
ACCRTW | Oswego/TW | 665 | 20 | 19 | 0.182 | 0.074 | 0.371 | 0.919 |  | 16 | 2 | 25 | 0.1348 | 75 | 0.1612 | 624 | 122.7
ACCRTW | Pecos/TW | 1622 | 38 | 19 | 0.2067 | 0.105 | 0.523 | 1.411 |  | 13 | 3 | 25 | 0.0584 | 75 | 0.069 | 1531 | 242.9
ACCRTW | Suwanee/TW | 958 | 24 | 19 | 0.1998 | 0.089 | 0.445 | 1.1099 |  | 16 | 2 | 25 | 0.0943 | 75 | 0.1125 | 899 | 175.9
ACCRTW | Wabash/TW | 763 | 20 | 19 | 0.195 | 0.083 | 0.416 | 0.99 |  | 17 | 2 | 25 | 0.117 | 75 | 0.1398 | 716 | 153.9
ACSR | Turkey | 6 | 6 | 1 | 0.0661 | 0.0661 | 0.0661 | 0.198 | 2.66 |  |  | 25 | 3.454 | 75 | 4.320 | 24.5 | 11.6
ACSR | Swan | 4 | 6 | 1 | 0.0834 | 0.0834 | 0.0834 | 0.25 | 3.35 |  |  | 25 | 2.172 | 75 | 2.765 | 38.9 | 18.4
ACSR | Swanate | 4 | 7 | 1 | 0.0772 | 0.1029 | 0.1029 | 0.257 | 3.45 |  |  | 25 | 2.147 | 75 | 2.779 | 38.9 | 28
ACSR | Sparrow | 2 | 6 | 1 | 0.1052 | 0.1052 | 0.1052 | 0.316 | 4.23 |  |  | 25 | 1.366 | 75 | 1.778 | 61.9 | 29.3
ACSR | Sparate | 2 | 7 | 1 | 0.0974 | 0.1299 | 0.1299 | 0.325 | 4.35 |  |  | 25 | 1.351 | 75 | 1.787 | 61.9 | 44.7
ACSR | Robin | 1 | 6 | 1 | 0.1181 | 0.1182 | 0.1182 | 0.355 | 4.75 |  |  | 25 | 1.083 | 75 | 1.427 | 78.1 | 37
ACSR | Raven | 1/0 | 6 | 1 | 0.1327 | 0.1327 | 0.1327 | 0.398 | 5.33 |  |  | 25 | 0.859 | 75 | 1.145 | 98.5 | 46.6
ACSR | Quail | 2/0 | 6 | 1 | 0.1489 | 0.1489 | 0.1489 | 0.447 | 5.99 |  |  | 25 | 0.681 | 75 | 0.924 | 124.1 | 58.7
ACSR | Pigeon | 3/0 | 6 | 1 | 0.1672 | 0.1672 | 0.1672 | 0.502 | 6.72 |  |  | 25 | 0.541 | 75 | 0.746 | 156.4 | 74
ACSR | Penguin | 4/0 | 6 | 1 | 0.1878 | 0.1878 | 0.1878 | 0.563 | 7.55 |  |  | 25 | 0.429 | 75 | 0.602 | 197.4 | 93.4
ACSR | Grouse | 80 | 8 | 1 | 0.100 | 0.167 | 0.167 | 0.367 | 4.77 |  |  | 25 | 1.112 | 75 | 1.525 | 75 | 73.9
ACSR | Petrel | 101.8 | 12 | 7 | 0.0921 | 0.0921 | 0.2763 | 0.461 | 5.76 |  |  | 25 | 0.853 | 75 | 1.321 | 95.9 | 157.9
ACSR | Minorca | 110.8 | 12 | 7 | 0.0961 | 0.0961 | 0.2883 | 0.481 | 6.01 |  |  | 25 | 0.783 | 75 | 1.233 | 104.4 | 171.9
ACSR | Leghorn | 134.6 | 12 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.53 | 6.62 |  |  | 25 | 0.645 | 75 | 1.053 | 126.8 | 208.7
ACSR | Guinea | 159 | 12 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.576 | 7.19 |  |  | 25 | 0.491 | 75 | 0.921 | 149.7 | 246.6
ACSR | Cochin | 211.3 | 12 | 7 | 0.1327 | 0.1327 | 0.3981 | 0.664 | 8.29 |  |  | 25 | 0.411 | 75 | 0.732 | 199 | 327.8
ACSR | Waxwing | 266.8 | 18 | 1 | 0.1217 | 0.1217 | 0.1217 | 0.609 |  |  |  | 25 | 0.3471 | 75 | 0.4155 | 249.9 | 39.2
ACSR | Partridge | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.3437 | 75 | 0.4113 | 251.3 | 115.6
ACSR | Junco | 266.8 | 30 | 7 | 0.0943 | 0.0943 | 0.2829 | 0.66 |  |  |  | 25 | 0.3413 | 75 | 0.4083 | 251.9 | 165.5
ACSR | Ostrich | 300.0 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.68 |  |  |  | 25 | 0.3058 | 75 | 0.3659 | 282.5 | 129.7
ACSR | Merlin | 336.4 | 18 | 1 | 0.1367 | 0.1367 | 0.1367 | 0.684 |  |  |  | 25 | 0.2756 | 75 | 0.3298 | 315.3 | 49.5
ACSR | Widgeon | 336.4 | 24 | 7 | 0.1184 | 0.0789 | 0.2367 | 0.7103 |  |  |  | 25 | 0.2740 | 75 | 0.3279 | 316.9 | 115.9
ACSR | Linnet | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.72 |  |  |  | 25 | 0.2728 | 75 | 0.3264 | 316.6 | 145.4
ACSR | Oriole | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.2708 | 75 | 0.3240 | 317.7 | 208.7
ACSR | Chickadee | 397.5 | 18 | 1 | 0.1486 | 0.1486 | 0.1486 | 0.743 |  |  |  | 25 | 0.2336 | 75 | 0.2794 | 372.5 | 58.5
ACSR | Brant | 397.5 | 24 | 7 | 0.1287 | 0.0858 | 0.2574 | 0.772 |  |  |  | 25 | 0.2321 | 75 | 0.2777 | 374.4 | 137
ACSR | Ibis | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2311 | 75 | 0.2764 | 374.1 | 171.9
ACSR | Lark | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2294 | 75 | 0.2743 | 375.3 | 246.5
ACSR | Pelican | 477.0 | 18 | 1 | 0.1628 | 0.1628 | 0.1628 | 0.814 |  |  |  | 25 | 0.1950 | 75 | 0.2331 | 447.1 | 70.2
ACSR | Flicker | 477.0 | 24 | 7 | 0.141 | 0.094 | 0.282 | 0.846 |  |  |  | 25 | 0.1937 | 75 | 0.2316 | 449.4 | 164.5
ACSR | Hawk | 477.0 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.1928 | 75 | 0.2305 | 449 | 206.4
ACSR | Hen | 477.0 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.1913 | 75 | 0.2288 | 450.4 | 296
ACSR | Osprey | 556.5 | 18 | 1 | 0.1758 | 0.1758 | 0.1758 | 0.879 |  |  |  | 25 | 0.1676 | 75 | 0.2002 | 521.4 | 81.8
ACSR | Parakeet | 556.5 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 0.914 |  |  |  | 25 | 0.1663 | 75 | 0.1988 | 524.3 | 191.8
ACSR | Dove | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1655 | 75 | 0.1978 | 524.2 | 241
ACSR | Eagle | 556.5 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 0.953 |  |  |  | 25 | 0.1642 | 75 | 0.1963 | 525.4 | 345.2
ACSR | Peacock | 605.0 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 0.953 |  |  |  | 25 | 0.1532 | 75 | 0.1830 | 570.1 | 208.7
ACSR | Squab | 605.0 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1524 | 75 | 0.1821 | 569.5 | 261.8
ACSR | Teal | 605.0 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1513 | 75 | 0.1808 | 571.2 | 367.4
ACSR | Wood Duck | 605.0 | 30 | 7 | 0.142 | 0.142 | 0.426 | 0.994 |  |  |  | 25 | 0.1512 | 75 | 0.1806 | 571.2 | 375.3
ACSR | Duck | 605.0 | 54 | 7 | 0.1058 | 0.1058 | 0.3174 | 0.952 |  |  |  | 25 | 0.1533 | 75 | 0.1880 | 569.3 | 208.3
ACSR | Kingbird | 636.0 | 18 | 1 | 0.188 | 0.188 | 0.188 | 0.94 |  |  |  | 25 | 0.1470 | 75 | 0.1755 | 596.3 | 93.6
ACSR | Rook | 636.0 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1458 | 75 | 0.1742 | 599.1 | 219.1
ACSR | Grosbeak | 636.0 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.99 |  |  |  | 25 | 0.1451 | 75 | 0.1733 | 599 | 275.2
ACSR | Scoter | 636.0 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.019 |  |  |  | 25 | 0.1439 | 75 | 0.1719 | 600.5 | 394.6
ACSR | Egret | 636.0 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1440 | 75 | 0.1720 | 600.5 | 386.7
ACSR | Swift | 636.0 | 36 | 1 | 0.1329 | 0.1329 | 0.1329 | 0.93 |  |  |  | 25 | 0.1477 | 75 | 0.1763 | 596 | 46.8
ACSR | Goose | 636.0 | 54 | 7 | 0.1085 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1459 | 75 | 0.1789 | 598.8 | 219.1
ACSR | Flamingo | 666.6 | 24 | 7 | 0.1667 | 0.1111 | 0.3333 | 1 |  |  |  | 25 | 0.1393 | 75 | 0.1663 | 628.2 | 229.7
ACSR | Gannet | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1385 | 75 | 0.1654 | 627.7 | 288.5
ACSR | Gull | 666.6 | 54 | 7 | 0.1111 | 0.1111 | 0.3333 | 0.9999 |  |  |  | 25 | 0.1394 | 75 | 0.1708 | 627.8 | 229.7
ACSR | Stilt | 715.5 | 24 | 7 | 0.1727 | 0.1151 | 0.3453 | 1.036 |  |  |  | 25 | 0.1299 | 75 | 0.1551 | 674.2 | 246.6
ACSR | Starling | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1292 | 75 | 0.1543 | 674 | 309.7
ACSR | Redwing | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1282 | 75 | 0.1531 | 675.3 | 434
ACSR | Crow | 715.5 | 54 | 7 | 0.1151 | 0.1151 | 0.345 | 1.04 |  |  |  | 25 | 0.1299 | 75 | 0.1592 | 673.8 | 246.5
ACSR | Turbit | 795.0 | 20 | 7 | 0.1994 | 0.0886 | 0.2658 | 1.0634 |  |  |  | 25 | 0.1185 | 75 | 0.1412 | 749 | 146.1
ACSR | Puffin | 795.0 | 22 | 7 | 0.1901 | 0.1056 | 0.3168 | 1.0772 |  |  |  | 25 | 0.1179 | 75 | 0.1405 | 748.8 | 207.6
ACSR | Cuckoo | 795.0 | 24 | 7 | 0.182 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1172 | 75 | 0.1398 | 748.8 | 273.9
ACSR | Drake | 795.0 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.1166 | 75 | 0.1390 | 749.1 | 344.3
ACSR | Skimmer | 795.0 | 30 | 7 | 0.1628 | 0.1628 | 0.4884 | 1.14 |  |  |  | 25 | 0.1155 | 75 | 0.1379 | 750.7 | 493.3
ACSR | Mallard | 795.0 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.14 |  |  |  | 25 | 0.1156 | 75 | 0.1380 | 750.7 | 483.2
ACSR | Coot | 795.0 | 36 | 1 | 0.1486 | 0.1486 | 0.1486 | 1.04 |  |  |  | 25 | 0.1190 | 75 | 0.1417 | 745.1 | 58.5
ACSR | Tern | 795.0 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1185 | 75 | 0.1421 | 748.6 | 146.1
ACSR | Condor | 795.0 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1172 | 75 | 0.1434 | 748.4 | 273.9
ACSR | Ruddy | 900.0 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1051 | 75 | 0.1259 | 847.4 | 165.5
ACSR | Canary | 900.0 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.1039 | 75 | 0.1269 | 847.7 | 310.2
ACSR | Corncrake | 954.0 | 20 | 7 | 0.2184 | 0.0971 | 0.291 | 1.165 |  |  |  | 25 | 0.0994 | 75 | 0.1183 | 898.5 | 175.5
ACSR | Redbird | 954.0 | 24 | 7 | 0.1994 | 0.1329 | 0.399 | 1.196 |  |  |  | 25 | 0.0982 | 75 | 0.1170 | 898.8 | 328.7
ACSR | Merganser | 954.0 | 30 | 7 | 0.1783 | 0.1783 | 0.5349 | 1.2481 |  |  |  | 25 | 0.0967 | 75 | 0.1152 | 900.5 | 591.7
ACSR | Rail | 954.0 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0994 | 75 | 0.1189 | 898.5 | 175.5
ACSR | Cardinal | 954.0 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0982 | 75 | 0.1199 | 898.3 | 328.7
ACSR | Snowbird | 1033.5 | 42 | 7 | 0.1569 | 0.0872 | 0.2616 | 1.203 |  |  |  | 25 | 0.0925 | 75 | 0.1105 | 973.9 | 141.5
ACSR | Ortolan | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.0921 | 75 | 0.1101 | 972.8 | 189.9
ACSR | Curlew | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.245 |  |  |  | 25 | 0.0910 | 75 | 0.1109 | 972.8 | 356
ACSR | Bluejay | 1113.0 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.259 |  |  |  | 25 | 0.0859 | 75 | 0.1025 | 1048.7 | 204.8
ACSR | Finch | 1113.0 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.293 |  |  |  | 25 | 0.0852 | 75 | 0.1039 | 1053.9 | 376.1
ACSR | Bunting | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0805 | 75 | 0.0959 | 1123.4 | 219.1
ACSR | Grackle | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.338 |  |  |  | 25 | 0.0798 | 75 | 0.0970 | 1128.6 | 402.8
ACSR | Bittern | 1272.0 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0759 | 75 | 0.0902 | 1197.7 | 233.9
ACSR | Pheasant | 1272.0 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.382 |  |  |  | 25 | 0.0751 | 75 | 0.0914 | 1204.3 | 429.4
ACSR | Dipper | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0718 | 75 | 0.0852 | 1272.9 | 248.3
ACSR | Martin | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0710 | 75 | 0.0860 | 1279.1 | 455.9
ACSR | Bobolink | 1431.0 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0681 | 75 | 0.0808 | 1347.5 | 263.1
ACSR | Plover | 1431.0 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0673 | 75 | 0.0814 | 1354.6 | 483.2
ACSR | Nuthatch | 1510.5 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0649 | 75 | 0.0768 | 1422.5 | 277.5
ACSR | Parrot | 1510.5 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0641 | 75 | 0.0774 | 1428.8 | 509.2
ACSR | Lapwing | 1590.0 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.0620 | 75 | 0.0733 | 1498.1 | 292.2
ACSR | Falcon | 1590.0 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.545 |  |  |  | 25 | 0.0611 | 75 | 0.0737 | 1505 | 537
ACSR | Chukar | 1780.0 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.602 |  |  |  | 25 | 0.0561 | 75 | 0.0658 | 1685.4 | 386.7
ACSR | Bluebird | 2156.0 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0477 | 75 | 0.0555 | 2040.4 | 467.5
ACSR | Kiwi | 2167.0 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0484 | 75 | 0.0562 | 2051.4 | 249.2
ACSR | Thrasher | 2312.0 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0457 | 75 | 0.0529 | 2187.9 | 335.4
ACSR | Joree | 2515.0 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.88 |  |  |  | 25 | 0.0428 | 75 | 0.0493 | 2380.1 | 364.9
ACSRAW | Swan/AW | 4 | 6 | 1 | 0.0834 | 0.0834 | 0.0834 | 0.25 | 3.35 |  |  | 25 | 2.1017 | 75 | 2.6801 | 38.9 | 15.6
ACSRAW | Swanate/AW | 4 | 7 | 1 | 0.0772 | 0.1029 | 0.1029 | 0.257 | 3.45 |  |  | 25 | 2.0448 | 75 | 2.6555 | 38.9 | 23.8
ACSRAW | Sparrow/AW | 2 | 6 | 1 | 0.1052 | 0.1052 | 0.1052 | 0.316 | 4.23 |  |  | 25 | 1.3220 | 75 | 1.7244 | 61.9 | 24.8
ACSRAW | Sparate/AW | 2 | 7 | 1 | 0.0974 | 0.1299 | 0.1299 | 0.325 | 4.35 |  |  | 25 | 1.2860 | 75 | 1.7096 | 61.9 | 37.9
ACSRAW | Robin/AW | 1 | 6 | 1 | 0.1182 | 0.1182 | 0.1182 | 0.355 | 4.75 |  |  | 25 | 1.0483 | 75 | 1.3844 | 78.2 | 31.4
ACSRAW | Raven/AW | 1/0 | 6 | 1 | 0.1327 | 0.1327 | 0.1327 | 0.398 | 5.33 |  |  | 25 | 0.8309 | 75 | 1.1119 | 98.5 | 39.5
ACSRAW | Penguin/AW | 4/0 | 6 | 1 | 0.1878 | 0.1878 | 0.1878 | 0.563 | 7.55 |  |  | 25 | 0.4150 | 75 | 0.5855 | 197.4 | 79.1
ACSRAW | Waxwing/AW | 266.8 | 18 | 1 | 0.1217 | 0.1217 | 0.1217 | 0.609 |  |  |  | 25 | 0.3433 | 75 | 0.4108 | 249.9 | 33.2
ACSRAW | Partridge/AW | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.3328 | 75 | 0.3981 | 251.3 | 97.9
ACSRAW | Ostrich/AW | 300 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.68 |  |  |  | 25 | 0.2961 | 75 | 0.3542 | 282.5 | 110
ACSRAW | Merlin/AW | 336.4 | 18 | 1 | 0.1367 | 0.1367 | 0.1367 | 0.684 |  |  |  | 25 | 0.2726 | 75 | 0.3261 | 315.3 | 41.9
ACSRAW | Linnet/AW | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.72 |  |  |  | 25 | 0.2642 | 75 | 0.3160 | 316.6 | 123.3
ACSRAW | Oriole/AW | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.2588 | 75 | 0.3095 | 317.7 | 176.9
ACSRAW | Chickadee/AW | 397.5 | 18 | 1 | 0.1486 | 0.1486 | 0.1486 | 0.743 |  |  |  | 25 | 0.2310 | 75 | 0.2762 | 372.6 | 49.6
ACSRAW | Brant/AW | 397.5 | 24 | 7 | 0.1287 | 0.0858 | 0.2574 | 0.772 |  |  |  | 25 | 0.2263 | 75 | 0.2706 | 374.4 | 116.1
ACSRAW | Ibis/AW | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2238 | 75 | 0.2676 | 374.1 | 145.7
ACSRAW | Lark/AW | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2192 | 75 | 0.2621 | 375.3 | 209
ACSRAW | Pelican/AW | 477 | 18 | 1 | 0.1628 | 0.1628 | 0.1628 | 0.814 |  |  |  | 25 | 0.1929 | 75 | 0.2305 | 447.2 | 59.5
ACSRAW | Flicker/AW | 477 | 24 | 7 | 0.141 | 0.094 | 0.282 | 0.846 |  |  |  | 25 | 0.1888 | 75 | 0.2257 | 449.4 | 139.4
ACSRAW | Hawk/AW | 477 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.1868 | 75 | 0.2232 | 449 | 174.9
ACSRAW | Hen/AW | 477 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.1829 | 75 | 0.2186 | 450.4 | 250.8
ACSRAW | Osprey/AW | 556.5 | 18 | 1 | 0.1758 | 0.1758 | 0.1758 | 0.879 |  |  |  | 25 | 0.1657 | 75 | 0.1979 | 521.4 | 69.4
ACSRAW | Parakeet/AW | 556.5 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 0.914 |  |  |  | 25 | 0.1622 | 75 | 0.1937 | 524.3 | 162.5
ACSRAW | Dove/AW | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1603 | 75 | 0.1915 | 524.2 | 204.3
ACSRAW | Eagle/AW | 556.5 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 0.953 |  |  |  | 25 | 0.1570 | 75 | 0.1875 | 525.5 | 292.6
ACSRAW | Peacock/AW | 605 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 0.953 |  |  |  | 25 | 0.1493 | 75 | 0.1783 | 570 | 176.9
ACSRAW | Squab/AW | 605 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1477 | 75 | 0.1763 | 569.5 | 221.9
ACSRAW | Teal/AW | 605 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1448 | 75 | 0.1729 | 571.2 | 311.4
ACSRAW | Kingbird/AW | 636 | 18 | 1 | 0.188 | 0.188 | 0.188 | 0.94 |  |  |  | 25 | 0.1454 | 75 | 0.1735 | 596.3 | 79.3
ACSRAW | Rook/AW | 636 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1422 | 75 | 0.1698 | 599.1 | 185.7
ACSRAW | Grosbeak/AW | 636 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.99 |  |  |  | 25 | 0.1406 | 75 | 0.1678 | 599 | 233.2
ACSRAW | Egret/AW | 636 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1378 | 75 | 0.1646 | 600.5 | 327.7
ACSRAW | Flamingo/AW | 666.6 | 24 | 7 | 0.1667 | 0.1111 | 0.3333 | 1 |  |  |  | 25 | 0.1358 | 75 | 0.1621 | 628.2 | 194.7
ACSRAW | Gannet/AW | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1342 | 75 | 0.1602 | 627.7 | 244.5
ACSRAW | Starling/AW | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1252 | 75 | 0.1494 | 674 | 262.5
ACSRAW | Redwing/AW | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1228 | 75 | 0.1465 | 675.3 | 367.9
ACSRAW | Crow/AW | 715.5 | 54 | 7 | 0.1151 | 0.1151 | 0.345 | 1.04 |  |  |  | 25 | 0.1267 | 75 | 0.1552 | 673.8 | 209
ACSRAW | Drake/AW | 795 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.1130 | 75 | 0.1347 | 749.1 | 291.7
ACSRAW | Mallard/AW | 795 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.14 |  |  |  | 25 | 0.1107 | 75 | 0.1320 | 750.7 | 409.5
ACSRAW | Tern/AW | 795 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1169 | 75 | 0.1401 | 748.6 | 123.8
ACSRAW | Condor/AW | 795 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1143 | 75 | 0.1398 | 748.4 | 232.1
ACSRAW | Ruddy/AW | 900 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1037 | 75 | 0.1243 | 847.4 | 140.3
ACSRAW | Canary/AW | 900 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.1014 | 75 | 0.1238 | 847.7 | 262.9
ACSRAW | Rail/AW | 954 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0981 | 75 | 0.1174 | 898.5 | 148.7
ACSRAW | Cardinal/AW | 954 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0958 | 75 | 0.1169 | 898.3 | 278.6
ACSRAW | Ortolan/AW | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.0909 | 75 | 0.1087 | 972.8 | 160.9
ACSRAW | Curlew/AW | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.245 |  |  |  | 25 | 0.0888 | 75 | 0.1081 | 972.8 | 301.7
ACSRAW | Bluejay/AW | 1113 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.259 |  |  |  | 25 | 0.0848 | 75 | 0.1011 | 1048.7 | 173.6
ACSRAW | Finch/AW | 1113 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.293 |  |  |  | 25 | 0.0832 | 75 | 0.1012 | 1053.9 | 318.8
ACSRAW | Bunting/AW | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0795 | 75 | 0.0948 | 1123.4 | 185.7
ACSRAW | Grackle/AW | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.333 |  |  |  | 25 | 0.0779 | 75 | 0.0946 | 1128.6 | 341.3
ACSRAW | Bittern/AW | 1272 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0749 | 75 | 0.0891 | 1197.7 | 198.2
ACSRAW | Pheasant/AW | 1272 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.382 |  |  |  | 25 | 0.0733 | 75 | 0.0889 | 1204.3 | 363.9
ACSRAW | Dipper/AW | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0708 | 75 | 0.0842 | 1272.9 | 210.4
ACSRAW | Martin/AW | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0693 | 75 | 0.0839 | 1279.1 | 386.4
ACSRAW | Bobolink/AW | 1431 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0673 | 75 | 0.0798 | 1347.5 | 223
ACSRAW | Plover/AW | 1431 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0658 | 75 | 0.0795 | 1354.6 | 409.5
ACSRAW | Nuthatch/AW | 1510.5 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0641 | 75 | 0.0759 | 1422.5 | 235.2
ACSRAW | Parrot/AW | 1510.5 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0626 | 75 | 0.0756 | 1428.8 | 431.6
ACSRAW | Lapwing/AW | 1590 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.0612 | 75 | 0.0724 | 1498.1 | 247.6
ACSRAW | Falcon/AW | 1590 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.545 |  |  |  | 25 | 0.0597 | 75 | 0.0720 | 1505 | 455.1
ACSRAW | Chukar/AW | 1780 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.602 |  |  |  | 25 | 0.0553 | 75 | 0.0649 | 1685.4 | 327.7
ACSRAW | Bluebird/AW | 2156 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0471 | 75 | 0.0548 | 2040.4 | 396.2
ACSRAW | Kiwi/AW | 2167 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0481 | 75 | 0.0558 | 2051.4 | 211.2
ACSRAW | Thrasher/AW | 2312 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0453 | 75 | 0.0524 | 2187.9 | 284.2
ACSRAW | Joree/AW | 2515 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.88 |  |  |  | 25 | 0.0424 | 75 | 0.0489 | 2380.1 | 309.2
ACSRTW | Athabaska/TW | 1949.6 | 42 | 7 |  | 0.1392 | 0.4176 | 1.504 |  | 7 | 3 | 25 | 0.0517 | 75 | 0.0607 | 1838 | 361
ACSRTW | Avocet/TW | 1113 | 30 | 7 |  | 0.0904 | 0.2712 | 1.129 |  | 5 | 3 | 25 | 0.0861 | 75 | 0.1045 | 1048.9 | 152.1
ACSRTW | Bittern/TW | 1272 | 35 | 7 |  | 0.1121 | 0.3363 | 1.22 |  | 7 | 3 | 25 | 0.0757 | 75 | 0.0917 | 1199 | 234
ACSRTW | Bluebird/TW | 2156 | 64 | 19 |  | 0.0961 | 0.4805 | 1.608 |  | 8 | 4 | 25 | 0.0475 | 75 | 0.0554 | 2047 | 468
ACSRTW | Bluejay/TW | 1113 | 33 | 7 |  | 0.1049 | 0.3147 | 1.143 |  | 7 | 3 | 25 | 0.0858 | 75 | 0.1042 | 1052.2 | 204.8
ACSRTW | Bobolink/TW | 1431 | 36 | 7 |  | 0.1189 | 0.3567 | 1.291 |  | 7 | 3 | 25 | 0.0679 | 75 | 0.0820 | 1350 | 263
ACSRTW | Bunting/TW | 1192.5 | 33 | 7 |  | 0.1085 | 0.3255 | 1.181 |  | 7 | 3 | 25 | 0.0804 | 75 | 0.0975 | 1124 | 219
ACSRTW | Calumet/TW | 565.3 | 20 | 7 |  | 0.1146 | 0.3441 | 0.858 |  | 16 | 2 | 25 | 0.1625 | 75 | 0.1941 | 531 | 244.8
ACSRTW | Cardinal/TW | 954 | 20 | 7 |  | 0.1329 | 0.3987 | 1.084 |  | 13 | 2 | 25 | 0.0977 | 75 | 0.1164 | 897.3 | 328.7
ACSRTW | Catawba/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0760 | 75 | 0.0920 | 1198 | 174
ACSRTW | Cheyenne/TW | 1168.1 | 30 | 7 |  | 0.0926 | 0.2778 | 1.155 |  | 5 | 3 | 25 | 0.0823 | 75 | 0.0998 | 1100.4 | 159.6
ACSRTW | Chukar/TW | 1780 | 37 | 19 |  | 0.0874 | 0.437 | 1.445 |  | 8 | 3 | 25 | 0.0555 | 75 | 0.0666 | 1676 | 387
ACSRTW | Columbia/TW | 966.2 | 21 | 7 |  | 0.1338 | 0.4014 | 1.092 |  | 13 | 2 | 25 | 0.0966 | 75 | 0.1150 | 908 | 333
ACSRTW | Condor/TW | 795 | 20 | 7 |  | 0.1213 | 0.3639 | 0.993 |  | 13 | 2 | 25 | 0.1167 | 75 | 0.1392 | 747.2 | 273.8
ACSRTW | Cumberland/TW | 1926.9 | 42 | 19 |  | 0.1133 | 0.5665 | 1.545 |  | 13 | 3 | 25 | 0.0511 | 75 | 0.0613 | 1821 | 650
ACSRTW | Curlew/TW | 1033.5 | 21 | 7 |  | 0.1363 | 0.4149 | 1.129 |  | 13 | 2 | 25 | 0.0905 | 75 | 0.1077 | 971.1 | 355.9
ACSRTW | Dipper/TW | 1351.5 | 35 | 7 |  | 0.1155 | 0.3465 | 1.256 |  | 7 | 3 | 25 | 0.0716 | 75 | 0.0865 | 1274 | 248
ACSRTW | Dove/TW | 556.5 | 20 | 7 |  | 0.1138 | 0.3414 | 0.852 |  | 16 | 2 | 25 | 0.1650 | 75 | 0.1972 | 523.5 | 241
ACSRTW | Drake/TW | 795 | 20 | 7 |  | 0.136 | 0.408 | 1.01 |  | 16 | 2 | 25 | 0.1161 | 75 | 0.1386 | 747.8 | 344.2
ACSRTW | Falcon/TW | 1590 | 42 | 19 |  | 0.103 | 0.515 | 1.408 |  | 13 | 3 | 25 | 0.0607 | 75 | 0.0733 | 1503 | 537
ACSRTW | Finch/TW | 1113 | 38 | 19 |  | 0.0862 | 0.431 | 1.185 |  | 13 | 3 | 25 | 0.0848 | 75 | 0.1032 | 1052.6 | 376.4
ACSRTW | Flicker/TW | 477 | 18 | 7 |  | 0.094 | 0.282 | 0.776 |  | 13 | 2 | 25 | 0.1930 | 75 | 0.2307 | 448.4 | 164.4
ACSRTW | Fraser/TW | 946.7 | 35 | 7 |  | 0.1154 | 0.3462 | 1.077 |  | 10 | 3 | 25 | 0.0995 | 75 | 0.1214 | 894 | 248
ACSRTW | Genesee/TW | 1158 | 33 | 7 |  | 0.1078 | 0.3234 | 1.165 |  | 7 | 3 | 25 | 0.0826 | 75 | 0.1003 | 1092 | 216
ACSRTW | Grackle/TW | 1192.5 | 38 | 19 |  | 0.0892 | 0.446 | 1.225 |  | 13 | 3 | 25 | 0.0794 | 75 | 0.0965 | 1127 | 403
ACSRTW | Grosbeak/TW | 636 | 20 | 7 |  | 0.1216 | 0.3648 | 0.908 |  | 16 | 2 | 25 | 0.1446 | 75 | 0.1727 | 598.4 | 275.1
ACSRTW | Hawk/TW | 477 | 18 | 7 |  | 0.1053 | 0.3159 | 0.789 |  | 16 | 2 | 25 | 0.1923 | 75 | 0.2298 | 448.7 | 206.3
ACSRTW | Hudson/TW | 1158.4 | 26 | 7 |  | 0.1467 | 0.4401 | 1.196 |  | 13 | 2 | 25 | 0.0811 | 75 | 0.0964 | 1089 | 400
ACSRTW | James/TW | 1730.6 | 39 | 19 |  | 0.1075 | 0.5375 | 1.47 |  | 13 | 3 | 25 | 0.0562 | 75 | 0.0677 | 1636 | 585
ACSRTW | Kettle/TW | 957.2 | 32 | 7 |  | 0.0973 | 0.2919 | 1.06 |  | 7 | 3 | 25 | 0.0990 | 75 | 0.1206 | 902.8 | 176.2
ACSRTW | Lapwing/TW | 1590 | 36 | 7 |  | 0.1253 | 0.3759 | 1.358 |  | 7 | 3 | 25 | 0.0618 | 75 | 0.0743 | 1499 | 292
ACSRTW | Mackenzie/TW | 1359.7 | 36 | 7 |  | 0.1159 | 0.3477 | 1.259 |  | 7 | 3 | 25 | 0.0712 | 75 | 0.0860 | 1280 | 250
ACSRTW | Martin/TW | 1351.5 | 39 | 19 |  | 0.0949 | 0.4745 | 1.3 |  | 13 | 3 | 25 | 0.0706 | 75 | 0.0856 | 1278 | 456
ACSRTW | Maumee/TW | 768.2 | 20 | 7 |  | 0.1195 | 0.3585 | 0.977 |  | 13 | 2 | 25 | 0.1207 | 75 | 0.1439 | 722.1 | 265.7
ACSRTW | Merlin/TW | 336.4 | 14 | 1 |  | 0.1367 | 0.1367 | 0.63 |  | 6 | 2 | 25 | 0.2756 | 75 | 0.3298 | 315.5 | 49.5
ACSRTW | Merrimack/TW | 1433.6 | 39 | 19 |  | 0.0978 | 0.489 | 1.34 |  | 13 | 3 | 25 | 0.0668 | 75 | 0.0809 | 1356 | 434
ACSRTW | Miramichi/TW | 1455.3 | 36 | 7 |  | 0.12 | 0.36 | 1.302 |  | 7 | 3 | 25 | 0.0669 | 75 | 0.0807 | 1372 | 268
ACSRTW | Mohawk/TW | 571.7 | 18 | 7 |  | 0.103 | 0.309 | 0.846 |  | 13 | 2 | 25 | 0.1613 | 75 | 0.1928 | 537.3 | 197.4
ACSRTW | Monongahela/TW | 405.1 | 14 | 1 |  | 0.152 | 0.152 | 0.68 |  | 6 | 2 | 25 | 0.2291 | 75 | 0.2740 | 379.8 | 61.2
ACSRTW | Mystic/TW | 666.6 | 20 | 7 |  | 0.1111 | 0.3333 | 0.913 |  | 13 | 2 | 25 | 0.1387 | 75 | 0.1656 | 626.6 | 229.7
ACSRTW | Nechako/TW | 768.9 | 27 | 1 |  | 0.152 | 0.152 | 0.93 |  | 3 | 3 | 25 | 0.1232 | 75 | 0.1506 | 720.7 | 61.2
ACSRTW | Nelson/TW | 1257.1 | 35 | 7 |  | 0.1115 | 0.3345 | 1.213 |  | 7 | 3 | 25 | 0.0765 | 75 | 0.0927 | 1185.7 | 231.3
ACSRTW | Ortolan/TW | 1033.5 | 32 | 7 |  | 0.101 | 0.303 | 1.102 |  | 7 | 3 | 25 | 0.0920 | 75 | 0.1120 | 975.2 | 189.8
ACSRTW | Oswego/TW | 664.8 | 20 | 7 |  | 0.1244 | 0.3732 | 0.927 |  | 16 | 2 | 25 | 0.1385 | 75 | 0.1653 | 625.4 | 288
ACSRTW | Oxbird/TW | 1192.5 | 30 | 7 |  | 0.0936 | 0.2808 | 1.167 |  | 5 | 3 | 25 | 0.0807 | 75 | 0.0978 | 1123 | 163
ACSRTW | Parakeet/TW | 556.5 | 18 | 7 |  | 0.1015 | 0.3045 | 0.835 |  | 13 | 2 | 25 | 0.1657 | 75 | 0.1980 | 523.2 | 191.7
ACSRTW | Pecos/TW | 1622 | 39 | 19 |  | 0.1064 | 0.532 | 1.424 |  | 13 | 3 | 25 | 0.0595 | 75 | 0.0718 | 1533 | 574
ACSRTW | Pee Dee/TW | 1758.6 | 37 | 7 |  | 0.1319 | 0.3957 | 1.427 |  | 7 | 3 | 25 | 0.0565 | 75 | 0.0677 | 1658 | 324
ACSRTW | Pheasant/TW | 1272 | 39 | 19 |  | 0.0921 | 0.4605 | 1.264 |  | 13 | 3 | 25 | 0.0747 | 75 | 0.0907 | 1202 | 430
ACSRTW | Phoenix/TW | 954 | 30 | 7 |  | 0.0837 | 0.2511 | 1.044 |  | 5 | 3 | 25 | 0.0996 | 75 | 0.1213 | 901.6 | 130.4
ACSRTW | Platte/TW | 1569 | 33 | 7 |  | 0.1074 | 0.3222 | 1.334 |  | 5 | 3 | 25 | 0.0629 | 75 | 0.0756 | 1478 | 215
ACSRTW | Plover/TW | 1431 | 39 | 19 |  | 0.0977 | 0.4885 | 1.337 |  | 13 | 3 | 25 | 0.0669 | 75 | 0.0810 | 1353 | 483
ACSRTW | Potomac/TW | 1557.4 | 36 | 7 |  | 0.1241 | 0.3723 | 1.345 |  | 7 | 3 | 25 | 0.0629 | 75 | 0.0757 | 1468 | 287
ACSRTW | Powder/TW | 2153.8 | 64 | 19 |  | 0.0961 | 0.4805 | 1.602 |  | 8 | 4 | 25 | 0.0475 | 75 | 0.0554 | 2030 | 468
ACSRTW | Puffin/TW | 795 | 18 | 7 |  | 0.1108 | 0.3324 | 0.98 |  | 10 | 2 | 25 | 0.1171 | 75 | 0.1396 | 746.9 | 228.4
ACSRTW | Rail/TW | 954 | 32 | 7 |  | 0.0971 | 0.2913 | 1.061 |  | 7 | 3 | 25 | 0.0993 | 75 | 0.1210 | 900 | 175
ACSRTW | Rio Grande/TW | 1533.3 | 39 | 19 |  | 0.1012 | 0.506 | 1.382 |  | 13 | 3 | 25 | 0.0628 | 75 | 0.0758 | 1449 | 519
ACSRTW | Rook/TW | 636 | 18 | 7 |  | 0.1085 | 0.3255 | 0.89 |  | 13 | 2 | 25 | 0.1452 | 75 | 0.1735 | 597.9 | 219.1
ACSRTW | Santee/TW | 2627.3 | 64 | 19 |  | 0.1062 | 0.531 | 1.762 |  | 8 | 4 | 25 | 0.0405 | 75 | 0.0468 | 2477 | 571
ACSRTW | Schuylkill/TW | 1657.4 | 36 | 7 |  | 0.128 | 0.384 | 1.386 |  | 7 | 3 | 25 | 0.0595 | 75 | 0.0715 | 1563 | 305
ACSRTW | Scissortail/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0760 | 75 | 0.0920 | 1198 | 174
ACSRTW | Snowbird/TW | 1033.5 | 30 | 7 |  | 0.0871 | 0.2613 | 1.089 |  | 5 | 3 | 25 | 0.0923 | 75 | 0.1123 | 973.8 | 141.2
ACSRTW | St. Croix/TW | 1467.8 | 33 | 7 |  | 0.1041 | 0.3123 | 1.292 |  | 5 | 3 | 25 | 0.0667 | 75 | 0.0804 | 1383 | 202
ACSRTW | Suwannee/TW | 959.6 | 22 | 7 |  | 0.1493 | 0.4479 | 1.108 |  | 16 | 2 | 25 | 0.0967 | 75 | 0.1152 | 903 | 415
ACSRTW | Swift/TW | 636 | 27 | 1 |  | 0.1329 | 0.1329 | 0.85 |  | 3 | 3 | 25 | 0.1482 | 75 | 0.1816 | 599.2 | 46.8
ACSRTW | Tern/TW | 795 | 17 | 7 |  | 0.0886 | 0.2658 | 0.96 |  | 7 | 2 | 25 | 0.1178 | 75 | 0.1405 | 745.9 | 146.1
ACSRTW | Thames/TW | 1334.6 | 39 | 19 |  | 0.0944 | 0.472 | 1.29 |  | 13 | 3 | 25 | 0.0714 | 75 | 0.0866 | 1261.6 | 451.4
ACSRTW | Truckee/TW | 1372.5 | 30 | 7 |  | 0.1004 | 0.3012 | 1.248 |  | 5 | 3 | 25 | 0.0709 | 75 | 0.0856 | 1293.4 | 187.6
ACSRTW | Wabash/TW | 762.8 | 20 | 7 |  | 0.1331 | 0.3343 | 0.99 |  | 16 | 2 | 25 | 0.1212 | 75 | 0.1446 | 717 | 330
ACSRTW | Yukon/TW | 1233.6 | 38 | 19 |  | 0.091 | 0.455 | 1.245 |  | 13 | 3 | 25 | 0.0769 | 75 | 0.0934 | 1166.5 | 419.5
ACSS | Bittern/ACSS | 1272 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0739 | 75 | 0.0884 | 1197.7 | 233.9
ACSS | Bluebird/ACSS | 2156 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0466 | 75 | 0.0544 | 2040.4 | 467.5
ACSS | Bluejay/ACSS | 1113 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.258 |  |  |  | 25 | 0.0837 | 75 | 0.1003 | 1048.7 | 204.8
ACSS | Bobolink/ACSS | 1431 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0664 | 75 | 0.0791 | 1347.5 | 263.1
ACSS | Brant/ACSS | 397.5 | 24 | 7 | 0.1287 | 0.0858 | 0.2574 | 0.772 |  |  |  | 25 | 0.2258 | 75 | 0.2714 | 374.4 | 137
ACSS | Bunting/ACSS | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0785 | 75 | 0.0939 | 1123.4 | 219.1
ACSS | Canary/ACSS | 900 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.1012 | 75 | 0.1245 | 847.7 | 310.2
ACSS | Canvasback/ACSS | 954 | 30 | 19 | 0.1783 | 0.107 | 0.535 | 1.248 |  |  |  | 25 | 0.0942 | 75 | 0.1128 | 900.5 | 579.6
ACSS | Cardinal/ACSS | 954 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0956 | 75 | 0.1176 | 898.3 | 328.7
ACSS | Chukar/ACSS | 1780 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.601 |  |  |  | 25 | 0.0547 | 75 | 0.0645 | 1685.4 | 386.7
ACSS | Condor/ACSS | 795 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1141 | 75 | 0.1406 | 748.4 | 273.9
ACSS | Corncrake/ACSS | 954 | 20 | 7 | 0.2184 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0968 | 75 | 0.1156 | 898.5 | 175.5
ACSS | Cuckoo/ACSS | 795 | 24 | 7 | 0.182 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1141 | 75 | 0.1367 | 748.8 | 273.9
ACSS | Curlew/ACSS | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.245 |  |  |  | 25 | 0.0886 | 75 | 0.1087 | 972.8 | 356
ACSS | Dipper/ACSS | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0699 | 75 | 0.0835 | 1272.9 | 248.3
ACSS | Dove/ACSS | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1610 | 75 | 0.1933 | 524.2 | 241
ACSS | Drake/ACSS | 795 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.1135 | 75 | 0.1359 | 749.1 | 344.3
ACSS | Egret/ACSS | 636 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1402 | 75 | 0.1682 | 600.5 | 386.7
ACSS | Falcon/ACSS | 1590 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.544 |  |  |  | 25 | 0.0596 | 75 | 0.0724 | 1505 | 537
ACSS | Finch/ACSS | 1113 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.292 |  |  |  | 25 | 0.0830 | 75 | 0.1017 | 1053.9 | 376.1
ACSS | Flamingo/ACSS | 666.6 | 24 | 7 | 0.1667 | 0.1111 | 0.3333 | 1.000 |  |  |  | 25 | 0.1355 | 75 | 0.1625 | 628.2 | 229.7
ACSS | Flicker/ACSS | 477 | 24 | 7 | 0.141 | 0.094 | 0.282 | 0.846 |  |  |  | 25 | 0.1885 | 75 | 0.2264 | 449.4 | 164.5
ACSS | Gannet/ACSS | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1348 | 75 | 0.1617 | 627.7 | 288.5
ACSS | Goldfinch/ACSS | 636 | 22 | 7 | 0.170 | 0.0944 | 0.2832 | 0.963 |  |  |  | 25 | 0.1426 | 75 | 0.1711 | 598.9 | 165.9
ACSS | Grackle/ACSS | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.337 |  |  |  | 25 | 0.0777 | 75 | 0.0951 | 1128.6 | 402.8
ACSS | Grosbeak/ACSS | 636 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.991 |  |  |  | 25 | 0.1412 | 75 | 0.1694 | 599 | 275.2
ACSS | Hawk/ACSS | 477 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.1876 | 75 | 0.2253 | 449 | 206.4
ACSS | Hen/ACSS | 477 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.1862 | 75 | 0.2236 | 450.4 | 296
ACSS | Ibis/ACSS | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2248 | 75 | 0.2701 | 374.1 | 171.9
ACSS | Joree/ACSS | 2515 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.880 |  |  |  | 25 | 0.0419 | 75 | 0.0484 | 2380.1 | 364.9
ACSS | Junco/ACSS | 266.8 | 30 | 7 | 0.0943 | 0.0943 | 0.2829 | 0.660 |  |  |  | 25 | 0.3320 | 75 | 0.3991 | 251.3 | 165.5
ACSS | Kiwi/ACSS | 2167 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0473 | 75 | 0.0551 | 2051.4 | 249.2
ACSS | Lapwing/ACSS | 1590 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.0605 | 75 | 0.0718 | 1498.1 | 292.2
ACSS | Lark/ACSS | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2232 | 75 | 0.2681 | 375.3 | 246.6
ACSS | Linnet/ACSS | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.720 |  |  |  | 25 | 0.2654 | 75 | 0.3190 | 316.6 | 145.5
ACSS | Macaw/ACSS | 795 | 42 | 7 | 0.1376 | 0.0764 | 0.2292 | 1.055 |  |  |  | 25 | 0.1157 | 75 | 0.1385 | 749 | 108.6
ACSS | Mallard/ACSS | 795 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.140 |  |  |  | 25 | 0.1125 | 75 | 0.1349 | 750.7 | 483.2
ACSS | Martin/ACSS | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0692 | 75 | 0.0844 | 1279.1 | 455.9
ACSS | Mockingbird/ACSS | 2034.5 | 72 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.681 |  |  |  | 25 | 0.0498 | 75 | 0.0581 | 1925.7 | 233.9
ACSS | Nuthatch/ACSS | 1510.5 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0633 | 75 | 0.0752 | 1422.5 | 277.5
ACSS | Oriole/ACSS | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.2635 | 75 | 0.3167 | 317.7 | 208.7
ACSS | Ortolan/ACSS | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.0897 | 75 | 0.1077 | 972.8 | 189.9
ACSS | Ostrich/ACSS | 300 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.680 |  |  |  | 25 | 0.2974 | 75 | 0.3575 | 282.5 | 129.8
ACSS | Parakeet/ACSS | 556.5 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 0.914 |  |  |  | 25 | 0.1618 | 75 | 0.1943 | 524.3 | 191.8
ACSS | Parrot/ACSS | 1510.5 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0624 | 75 | 0.0759 | 1428.8 | 509.2
ACSS | Partridge/ACSS | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.3343 | 75 | 0.4019 | 251.3 | 115.6
ACSS | Peacock/ACSS | 605 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 0.953 |  |  |  | 25 | 0.1490 | 75 | 0.1789 | 570 | 208.7
ACSS | Pheasant/ACSS | 1272 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.381 |  |  |  | 25 | 0.0732 | 75 | 0.0894 | 1204.3 | 429.4
ACSS | Plover/ACSS | 1431 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0656 | 75 | 0.0799 | 1354.6 | 483.2
ACSS | Ptarmigan/ACSS | 397.5 | 20 | 7 | 0.141 | 0.0627 | 0.1881 | 0.752 |  |  |  | 25 | 0.2277 | 75 | 0.2737 | 374.5 | 73.2
ACSS | Puffin/ACSS | 795 | 22 | 7 | 0.1901 | 0.1056 | 0.3168 | 1.077 |  |  |  | 25 | 0.1147 | 75 | 0.1374 | 748.8 | 207.6
ACSS | Rail/ACSS | 954 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0968 | 75 | 0.1164 | 898.5 | 175.5
ACSS | Ratite/ACSS | 1590 | 42 | 7 | 0.1946 | 0.1081 | 0.3243 | 1.492 |  |  |  | 25 | 0.0608 | 75 | 0.0718 | 1498.1 | 217.5
ACSS | Redbird/ACSS | 954 | 24 | 7 | 0.1994 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0956 | 75 | 0.1144 | 898.8 | 328.7
ACSS | Redwing/ACSS | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1248 | 75 | 0.1497 | 675.3 | 434.1
ACSS | Roadrunner/ACSS | 2057 | 76 | 19 | 0.1645 | 0.0768 | 0.384 | 1.700 |  |  |  | 25 | 0.0490 | 75 | 0.0573 | 1946.5 | 298.6
ACSS | Rook/ACSS | 636 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1419 | 75 | 0.1702 | 599.1 | 219.1
ACSS | Ruddy/ACSS | 900 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1023 | 75 | 0.1232 | 847.4 | 165.5
ACSS | Sapsucker/ACSS | 556.5 | 22 | 7 | 0.159 | 0.0883 | 0.2649 | 0.901 |  |  |  | 25 | 0.1626 | 75 | 0.1952 | 523.9 | 145.1
ACSS | Scoter/ACSS | 636 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.019 |  |  |  | 25 | 0.1401 | 75 | 0.1681 | 600.5 | 394.6
ACSS | Snowbird/ACSS | 1033.5 | 42 | 7 | 0.1569 | 0.0872 | 0.2616 | 1.203 |  |  |  | 25 | 0.0901 | 75 | 0.1074 | 973.9 | 141.5
ACSS | Squab/ACSS | 605 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1483 | 75 | 0.1780 | 569.5 | 261.8
ACSS | Starling/ACSS | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1258 | 75 | 0.1508 | 674 | 309.7
ACSS | Stilt/ACSS | 715.5 | 24 | 7 | 0.1727 | 0.1151 | 0.3453 | 1.036 |  |  |  | 25 | 0.1264 | 75 | 0.1516 | 674.2 | 246.6
ACSS | Tailorbird/ACSS | 477 | 20 | 7 | 0.1544 | 0.0686 | 0.2058 | 0.824 |  |  |  | 25 | 0.1901 | 75 | 0.2284 | 449.1 | 87.6
ACSS | Teal/ACSS | 605 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1472 | 75 | 0.1767 | 571.2 | 367.5
ACSS | Tern/ACSS | 795 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1153 | 75 | 0.1390 | 748.6 | 146.1
ACSS | Thrasher/ACSS | 2312 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0447 | 75 | 0.0519 | 2187.9 | 335.4
ACSS | Towhee/ACSS | 954 | 48 | 7 | 0.141 | 0.1097 | 0.3291 | 1.175 |  |  |  | 25 | 0.0964 | 75 | 0.1152 | 898.8 | 224
ACSS | Wood Duck/ACSS | 605 | 30 | 7 | 0.142 | 0.142 | 0.426 | 0.994 |  |  |  | 25 | 0.1471 | 75 | 0.1766 | 571.2 | 375.3
ACSS | WoodCock/ACSS | 336.4 | 22 | 7 | 0.1237 | 0.0687 | 0.2061 | 0.701 |  |  |  | 25 | 0.2677 | 75 | 0.3218 | 317.1 | 87.8
ACSSAW | Bittern/ACSS/AW | 1272 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0730 | 75 | 0.0872 | 1197.7 | 198.2
ACSSAW | Bluebird/ACSS/AW | 2156 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0460 | 75 | 0.0537 | 2040.4 | 396.1
ACSSAW | Bluejay/ACSS/AW | 1113 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.259 |  |  |  | 25 | 0.0826 | 75 | 0.0990 | 1048.7 | 173.5
ACSSAW | Bobolink/ACSS/AW | 1431 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0656 | 75 | 0.0781 | 1347.5 | 223
ACSSAW | Brant/ACSS/AW | 397.5 | 24 | 7 | 0.1287 | 0.0858 | 0.2574 | 0.772 |  |  |  | 25 | 0.2202 | 75 | 0.2646 | 374.4 | 116.1
ACSSAW | Bunting/ACSS/AW | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0775 | 75 | 0.0927 | 1123.4 | 185.7
ACSSAW | Canary/ACSS/AW | 900 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.0987 | 75 | 0.1214 | 847.7 | 262.9
ACSSAW | Canvasback/ACSS/AW | 954 | 30 | 19 | 0.1783 | 0.107 | 0.535 | 1.248 |  |  |  | 25 | 0.0903 | 75 | 0.1080 | 900.5 | 491.1
ACSSAW | Cardinal/ACSS/AW | 954 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0934 | 75 | 0.1147 | 898.3 | 278.6
ACSSAW | Chukar/ACSS/AW | 1780 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.602 |  |  |  | 25 | 0.0540 | 75 | 0.0635 | 1685.4 | 327.6
ACSSAW | Condor/ACSS/AW | 795 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1113 | 75 | 0.1372 | 748.4 | 232.1
ACSSAW | Corncrake/ACSS/AW | 954 | 20 | 7 | 0.2184 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0956 | 75 | 0.1141 | 898.5 | 148.7
ACSSAW | Cuckoo/ACSS/AW | 795 | 24 | 7 | 0.182 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1113 | 75 | 0.1333 | 748.8 | 232.1
ACSSAW | Curlew/ACSS/AW | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.245 |  |  |  | 25 | 0.0865 | 75 | 0.1061 | 972.8 | 301.7
ACSSAW | Dipper/ACSS/AW | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0691 | 75 | 0.0824 | 1272.9 | 210.4
ACSSAW | Dove/ACSS/AW | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1561 | 75 | 0.1873 | 524.2 | 204.2
ACSSAW | Drake/ACSS/AW | 795 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.1100 | 75 | 0.1318 | 749.1 | 291.7
ACSSAW | Eagle/ACSS/AW | 556.5 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 0.953 |  |  |  | 25 | 0.1530 | 75 | 0.1835 | 525.5 | 292.6
ACSSAW | Egret/ACSS/AW | 636 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1343 | 75 | 0.1610 | 600.5 | 327.6
ACSSAW | Falcon/ACSS/AW | 1590 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.544 |  |  |  | 25 | 0.0583 | 75 | 0.0707 | 1505 | 455
ACSSAW | Finch/ACSS/AW | 1113 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.293 |  |  |  | 25 | 0.0810 | 75 | 0.0993 | 1053.9 | 318.7
ACSSAW | Flamingo/ACSS/AW | 666.6 | 24 | 7 | 0.1667 | 0.1111 | 0.3333 | 1.000 |  |  |  | 25 | 0.1322 | 75 | 0.1585 | 628.2 | 194.7
ACSSAW | Flicker/ACSS/AW | 477 | 24 | 7 | 0.141 | 0.094 | 0.282 | 0.846 |  |  |  | 25 | 0.1838 | 75 | 0.2207 | 449.4 | 139.4
ACSSAW | Gannet/ACSS/AW | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1307 | 75 | 0.1567 | 627.7 | 244.5
ACSSAW | Goldfinch/ACSS/AW | 636 | 22 | 7 | 0.170 | 0.0944 | 0.2832 | 0.963 |  |  |  | 25 | 0.1400 | 75 | 0.1678 | 598.9 | 140.5
ACSSAW | Grackle/ACSS/AW | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.338 |  |  |  | 25 | 0.0760 | 75 | 0.0929 | 1128.6 | 341.3
ACSSAW | Grosbeak/ACSS/AW | 636 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.990 |  |  |  | 25 | 0.1369 | 75 | 0.1642 | 599 | 233.2
ACSSAW | Hawk/ACSS/AW | 477 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.1818 | 75 | 0.2183 | 449 | 174.9
ACSSAW | Hen/ACSS/AW | 477 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.1782 | 75 | 0.2139 | 450.4 | 250.8
ACSSAW | Ibis/ACSS/AW | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2179 | 75 | 0.2617 | 374.1 | 145.6
ACSSAW | Joree/ACSS/AW | 2515 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.880 |  |  |  | 25 | 0.0415 | 75 | 0.0480 | 2380.1 | 309.2
ACSSAW | Junco/ACSS/AW | 266.8 | 30 | 7 | 0.0943 | 0.0943 | 0.2829 | 0.660 |  |  |  | 25 | 0.3176 | 75 | 0.3816 | 251.3 | 140.2
ACSSAW | Kiwi/ACSS/AW | 2167 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0470 | 75 | 0.0547 | 2051.4 | 211.1
ACSSAW | Lapwing/ACSS/AW | 1590 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.0597 | 75 | 0.0709 | 1498.1 | 247.6
ACSSAW | Lark/ACSS/AW | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2135 | 75 | 0.2564 | 375.3 | 208.9
ACSSAW | Linnet/ACSS/AW | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.720 |  |  |  | 25 | 0.2572 | 75 | 0.3090 | 316.6 | 123.2
ACSSAW | Macaw/ACSS/AW | 795 | 42 | 7 | 0.1376 | 0.0764 | 0.2292 | 1.055 |  |  |  | 25 | 0.1146 | 75 | 0.1371 | 749 | 92.1
ACSSAW | Mallard/ACSS/AW | 795 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.140 |  |  |  | 25 | 0.1079 | 75 | 0.1292 | 750.7 | 409.4
ACSSAW | Martin/ACSS/AW | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0676 | 75 | 0.0824 | 1279.1 | 386.3
ACSSAW | Mockingbird/ACSS/AW | 2034.5 | 72 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.681 |  |  |  | 25 | 0.0494 | 75 | 0.0577 | 1925.7 | 198.2
ACSSAW | Nuthatch/ACSS/AW | 1510 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0625 | 75 | 0.0743 | 1422.5 | 235.1
ACSSAW | Oriole/ACSS/AW | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.2521 | 75 | 0.3028 | 317.7 | 176.9
ACSSAW | Ortolan/ACSS/AW | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.0886 | 75 | 0.1063 | 972.8 | 160.9
ACSSAW | Ostrich/ACSS/AW | 300 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.680 |  |  |  | 25 | 0.2883 | 75 | 0.3464 | 282.5 | 110
ACSSAW | Parakeet/ACSS/AW | 556.5 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 0.914 |  |  |  | 25 | 0.1579 | 75 | 0.1894 | 524.3 | 162.5
ACSSAW | Parrot/ACSS/AW | 1510 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0611 | 75 | 0.0742 | 1428.8 | 431.5
ACSSAW | Partridge/ACSS/AW | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.3240 | 75 | 0.3894 | 251.3 | 97.9
ACSSAW | Peacock/ACSS/AW | 605 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 0.953 |  |  |  | 25 | 0.1454 | 75 | 0.1744 | 570 | 176.9
ACSSAW | Pheasant/ACSS/AW | 1272 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.382 |  |  |  | 25 | 0.0715 | 75 | 0.0873 | 1204.3 | 363.8
ACSSAW | Plover/ACSS/AW | 1431 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0641 | 75 | 0.0781 | 1354.6 | 409.4
ACSSAW | Ptarmigan/ACSS/AW | 397.5 | 20 | 7 | 0.141 | 0.0627 | 0.1881 | 0.752 |  |  |  | 25 | 0.2247 | 75 | 0.2700 | 374.5 | 62
ACSSAW | Rail/ACSS/AW | 954 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0956 | 75 | 0.1149 | 898.5 | 148.7
ACSSAW | Ratite/ACSS/AW | 1590 | 42 | 7 | 0.1946 | 0.1081 | 0.3243 | 1.492 |  |  |  | 25 | 0.0603 | 75 | 0.0711 | 1498.1 | 184.3
ACSSAW | Redbird/ACSS/AW | 954 | 24 | 7 | 0.1994 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0934 | 75 | 0.1116 | 898.8 | 278.6
ACSSAW | Redwing/ACSS/AW | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1196 | 75 | 0.1434 | 675.3 | 367.8
ACSSAW | Roadrunner/ACSS/AW | 2057 | 76 | 19 | 0.1645 | 0.0768 | 0.384 | 1.700 |  |  |  | 25 | 0.0486 | 75 | 0.0568 | 1946.5 | 253
ACSSAW | Rook/ACSS/AW | 636 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1384 | 75 | 0.1660 | 599.1 | 185.7
ACSSAW | Ruddy/ACSS/AW | 900 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1010 | 75 | 0.1216 | 847.4 | 140.2
ACSSAW | Sapsucker/ACSS/AW | 556.5 | 22 | 7 | 0.159 | 0.0883 | 0.2649 | 0.901 |  |  |  | 25 | 0.1596 | 75 | 0.1915 | 523.9 | 123
ACSSAW | Scoter/ACSS/AW | 636 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.019 |  |  |  | 25 | 0.1341 | 75 | 0.1608 | 600.5 | 334.3
ACSSAW | Snowbird/ACSS/AW | 1033.5 | 42 | 7 | 0.1569 | 0.0872 | 0.2616 | 1.203 |  |  |  | 25 | 0.0892 | 75 | 0.1064 | 973.9 | 119.9
ACSSAW | Squab/ACSS/AW | 605 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1438 | 75 | 0.1725 | 569.5 | 221.8
ACSSAW | Starling/ACSS/AW | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1220 | 75 | 0.1462 | 674 | 262.4
ACSSAW | Stilt/ACSS/AW | 715.5 | 24 | 7 | 0.1727 | 0.1151 | 0.3453 | 1.036 |  |  |  | 25 | 0.1234 | 75 | 0.1478 | 674.2 | 208.9
ACSSAW | Tailorbird/ACSS/AW | 477 | 20 | 7 | 0.1544 | 0.0686 | 0.2058 | 0.823 |  |  |  | 25 | 0.1876 | 75 | 0.2253 | 449.1 | 74.2
ACSSAW | Teal/ACSS/AW | 605 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1411 | 75 | 0.1692 | 571.2 | 311.4
ACSSAW | Tern/ACSS/AW | 795 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1138 | 75 | 0.1372 | 748.6 | 123.8
ACSSAW | Thrasher/ACSS/AW | 2312 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0443 | 75 | 0.0514 | 2187.9 | 284.2
ACSSAW | Towhee/ACSS/AW | 954 | 48 | 7 | 0.141 | 0.1097 | 0.3291 | 1.175 |  |  |  | 25 | 0.0948 | 75 | 0.1132 | 898.8 | 189.8
ACSSAW | Wood Duck/ACSS/AW | 605 | 30 | 7 | 0.142 | 0.142 | 0.426 | 0.994 |  |  |  | 25 | 0.1408 | 75 | 0.1689 | 571.2 | 318
ACSSAW | WoodCock/ACSS/AW | 336.4 | 22 | 7 | 0.1237 | 0.0687 | 0.2061 | 0.701 |  |  |  | 25 | 0.2626 | 75 | 0.3156 | 317.1 | 74.4
ACSSAWTW | Athabaska/ACSS/AW/TW | 1949.6 | 42 | 7 |  | 0.1392 | 0.4176 | 1.504 |  | 7 | 3 | 25 | 0.0499 | 75 | 0.0587 | 1836.3 | 305.6
ACSSAWTW | Avocet/ACSS/AW/TW | 1113 | 30 | 7 |  | 0.0904 | 0.2712 | 1.129 |  | 5 | 3 | 25 | 0.0831 | 75 | 0.1012 | 1047.3 | 128.9
ACSSAWTW | Bittern/ACSS/AW/TW | 1272 | 35 | 7 |  | 0.1121 | 0.3363 | 1.22 |  | 7 | 3 | 25 | 0.0729 | 75 | 0.0885 | 1198.1 | 198.2
ACSSAWTW | Bluebird/ACSS/AW/TW | 2156 | 64 | 19 |  | 0.0961 | 0.4805 | 1.608 |  | 8 | 4 | 25 | 0.0458 | 75 | 0.0535 | 2044.6 | 396.1
ACSSAWTW | Bluejay/ACSS/AW/TW | 1113 | 33 | 7 |  | 0.1049 | 0.3147 | 1.143 |  | 7 | 3 | 25 | 0.0825 | 75 | 0.1006 | 1048.3 | 173.5
ACSSAWTW | Bobolink/ACSS/AW/TW | 1431 | 36 | 7 |  | 0.1189 | 0.3567 | 1.291 |  | 7 | 3 | 25 | 0.0654 | 75 | 0.0792 | 1347.8 | 223
ACSSAWTW | Bunting/ACSS/AW/TW | 1192.5 | 33 | 7 |  | 0.1085 | 0.3255 | 1.181 |  | 7 | 3 | 25 | 0.0773 | 75 | 0.0941 | 1123.2 | 185.7
ACSSAWTW | Calumet/ACSS/AW/TW | 565.3 | 20 | 7 |  | 0.1146 | 0.3441 | 0.858 |  | 16 | 2 | 25 | 0.1533 | 75 | 0.1839 | 531.2 | 207.5
ACSSAWTW | Canary/ACSS/AW/TW | 900 | 20 | 7 |  | 0.1291 | 0.3873 | 1.055 |  | 13 | 3 | 25 | 0.0989 | 75 | 0.1212 | 845.6 | 262.9
ACSSAWTW | Cardinal/ACSS/AW/TW | 954 | 20 | 7 |  | 0.1329 | 0.3987 | 1.084 |  | 13 | 2 | 25 | 0.0929 | 75 | 0.1111 | 895.5 | 278.6
ACSSAWTW | Catawba/ACSS/AW/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0734 | 75 | 0.0891 | 1196.9 | 147.5
ACSSAWTW | Cheyenne/ACSS/AW/TW | 1168.1 | 30 | 7 |  | 0.0926 | 0.2778 | 1.155 |  | 5 | 3 | 25 | 0.0794 | 75 | 0.0967 | 1099 | 135.2
ACSSAWTW | Chukar/ACSS/AW/TW | 1780 | 37 | 19 |  | 0.0874 | 0.437 | 1.445 |  | 8 | 3 | 25 | 0.0534 | 75 | 0.0643 | 1674.1 | 327.6
ACSSAWTW | Columbia/ACSS/AW/TW | 966.2 | 21 | 7 |  | 0.1338 | 0.4014 | 1.092 |  | 13 | 2 | 25 | 0.0917 | 75 | 0.1097 | 906.9 | 282.3
ACSSAWTW | Condor/ACSS/AW/TW | 795 | 20 | 7 |  | 0.1213 | 0.3639 | 0.993 |  | 13 | 2 | 25 | 0.1108 | 75 | 0.1327 | 746.3 | 232.1
ACSSAWTW | Cumberland/ACSS/AW/TW | 1926.9 | 42 | 19 |  | 0.1133 | 0.5665 | 1.545 |  | 13 | 3 | 25 | 0.0488 | 75 | 0.0587 | 1819.4 | 550.6
ACSSAWTW | Curlew/ACSS/AW/TW | 1033.5 | 20 | 7 |  | 0.1383 | 0.4149 | 1.129 |  | 13 | 2 | 25 | 0.0860 | 75 | 0.1027 | 970.1 | 301.7
ACSSAWTW | Dipper/ACSS/AW/TW | 1351.5 | 35 | 7 |  | 0.1155 | 0.3465 | 1.256 |  | 7 | 3 | 25 | 0.0689 | 75 | 0.0836 | 1273 | 210.4
ACSSAWTW | Dove/ACSS/AW/TW | 556.5 | 20 | 7 |  | 0.1138 | 0.3414 | 0.852 |  | 16 | 2 | 25 | 0.1557 | 75 | 0.1868 | 522.9 | 204.2
ACSSAWTW | Drake/ACSS/AW/TW | 795 | 20 | 7 |  | 0.136 | 0.408 | 1.010 |  | 16 | 2 | 25 | 0.1096 | 75 | 0.1313 | 747.0 | 291.7
ACSSAWTW | Falcon/ACSS/AW/TW | 1590 | 42 | 19 |  | 0.103 | 0.515 | 1.408 |  | 13 | 3 | 25 | 0.0579 | 75 | 0.0701 | 1501.3 | 455.0
ACSSAWTW | Finch/ACSS/AW/TW | 1113 | 38 | 19 |  | 0.0862 | 0.431 | 1.185 |  | 13 | 3 | 25 | 0.0807 | 75 | 0.0986 | 1051 | 318.7
ACSSAWTW | Flicker/ACSS/AW/TW | 477 | 18 | 7 |  | 0.094 | 0.282 | 0.776 |  | 13 | 2 | 25 | 0.1831 | 75 | 0.2199 | 447.8 | 139.4
ACSSAWTW | Fraser/ACSS/AW/TW | 946.7 | 35 | 7 |  | 0.1154 | 0.3462 | 1.077 |  | 10 | 3 | 25 | 0.0951 | 75 | 0.1165 | 892.6 | 210.0
ACSSAWTW | Genesee/ACSS/AW/TW | 1158 | 33 | 7 |  | 0.1078 | 0.3234 | 1.165 |  | 7 | 3 | 25 | 0.0795 | 75 | 0.0968 | 1091 | 183.3
ACSSAWTW | Grackle/ACSS/AW/TW | 1192.5 | 38 | 19 |  | 0.0892 | 0.446 | 1.225 |  | 13 | 3 | 25 | 0.0756 | 75 | 0.0922 | 1126 | 341.3
ACSSAWTW | Grosbeak/ACSS/AW/TW | 636 | 20 | 7 |  | 0.1216 | 0.3648 | 0.908 |  | 16 | 2 | 25 | 0.1365 | 75 | 0.1637 | 597.6 | 233.2
ACSSAWTW | Hawk/ACSS/AW/TW | 477 | 18 | 7 |  | 0.1053 | 0.3159 | 0.789 |  | 16 | 2 | 25 | 0.1813 | 75 | 0.2177 | 448.1 | 174.9
ACSSAWTW | Hen/ACSS/AW/TW | 477 | 16 | 7 |  | 0.1261 | 0.3783 | 0.825 |  | 23 | 2 | 25 | 0.1773 | 75 | 0.2128 | 448.3 | 250.8
ACSSAWTW | Hudson/ACSS/AW/TW | 1158.4 | 25 | 7 |  | 0.1467 | 0.4401 | 1.196 |  | 13 | 2 | 25 | 0.0772 | 75 | 0.0920 | 1087.4 | 339.4
ACSSAWTW | James/ACSS/AW/TW | 1730.6 | 39 | 19 |  | 0.1075 | 0.5375 | 1.470 |  | 13 | 3 | 25 | 0.0537 | 75 | 0.0648 | 1634 | 495.7
ACSSAWTW | Kettle/ACSS/AW/TW | 957.2 | 32 | 7 |  | 0.0973 | 0.2919 | 1.060 |  | 7 | 3 | 25 | 0.0952 | 75 | 0.1164 | 901.6 | 149.3
ACSSAWTW | Lapwing/ACSS/AW/TW | 1590 | 36 | 7 |  | 0.1253 | 0.3759 | 1.358 |  | 7 | 3 | 25 | 0.0595 | 75 | 0.0718 | 1497.6 | 247.6
ACSSAWTW | Linnet/ACSS/AW/TW | 336.4 | 18 | 7 |  | 0.0884 | 0.2652 | 0.659 |  | 16 | 2 | 25 | 0.2566 | 75 | 0.3083 | 315.9 | 123.2
ACSSAWTW | Mackenzie/ACSS/AW/TW | 1359.7 | 36 | 7 |  | 0.1159 | 0.3477 | 1.259 |  | 7 | 3 | 25 | 0.0685 | 75 | 0.0831 | 1281 | 211.9
ACSSAWTW | Martin/ACSS/AW/TW | 1351.5 | 39 | 19 |  | 0.0949 | 0.4745 | 1.300 |  | 13 | 3 | 25 | 0.0672 | 75 | 0.0818 | 1276 | 386.3
ACSSAWTW | Maumee/ACSS/AW/TW | 768.2 | 20 | 7 |  | 0.1195 | 0.3585 | 0.977 |  | 13 | 2 | 25 | 0.1146 | 75 | 0.1373 | 721.1 | 225.2
ACSSAWTW | Merrimack/ACSS/AW/TW | 1433.6 | 39 | 19 |  | 0.0978 | 0.489 | 1.340 |  | 13 | 3 | 25 | 0.0637 | 75 | 0.0773 | 1353.6 | 410.3
ACSSAWTW | MiramichiACSS/AW/TW | 1455.3 | 36 | 7 |  | 0.120 | 0.360 | 1.302 |  | 7 | 3 | 25 | 0.0644 | 75 | 0.0780 | 1371 | 227.1
ACSSAWTW | Mohawk/ACSS/AW/TW | 571.7 | 18 | 7 |  | 0.103 | 0.309 | 0.846 |  | 13 | 2 | 25 | 0.1531 | 75 | 0.1837 | 536.6 | 167.3
ACSSAWTW | Mystic/ACSS/AW/TW | 666.6 | 20 | 7 |  | 0.1111 | 0.3333 | 0.913 |  | 13 | 2 | 25 | 0.1317 | 75 | 0.1579 | 625.7 | 194.7
ACSSAWTW | Nelson/ACSS/AW/TW | 1257.1 | 35 | 7 |  | 0.1115 | 0.3345 | 1.213 |  | 7 | 3 | 25 | 0.0736 | 75 | 0.0895 | 1184 | 196.1
ACSSAWTW | Oriole/ACSS/AW/TW | 336.4 | 16 | 7 |  | 0.1059 | 0.3177 | 0.693 |  | 23 | 2 | 25 | 0.2509 | 75 | 0.3014 | 316.1 | 176.9
ACSSAWTW | Ortolan/ACSS/AW/TW | 1033.5 | 32 | 7 |  | 0.101 | 0.303 | 1.102 |  | 7 | 3 | 25 | 0.0885 | 75 | 0.1081 | 973.4 | 160.9
ACSSAWTW | Oswego/ACSS/AW/TW | 664.8 | 20 | 7 |  | 0.1244 | 0.3732 | 0.927 |  | 16 | 2 | 25 | 0.1306 | 75 | 0.1567 | 624.6 | 244.1
ACSSAWTW | Oxbird/ACSS/AW/TW | 1192.5 | 30 | 7 |  | 0.0936 | 0.2808 | 1.167 |  | 5 | 3 | 25 | 0.0779 | 75 | 0.0948 | 1122 | 138.2
ACSSAWTW | Parakeet/ACSS/AW/TW | 556.5 | 18 | 7 |  | 0.1015 | 0.3045 | 0.835 |  | 13 | 2 | 25 | 0.1573 | 75 | 0.1887 | 522.4 | 162.5
ACSSAWTW | Pecos/ACSS/AW/TW | 1622 | 39 | 19 |  | 0.1064 | 0.532 | 1.424 |  | 13 | 3 | 25 | 0.0567 | 75 | 0.0686 | 1531.5 | 485.6
ACSSAWTW | Pee Dee/ACSS/AW/TW | 1758.6 | 37 | 7 |  | 0.1319 | 0.3957 | 1.427 |  | 7 | 3 | 25 | 0.0545 | 75 | 0.0655 | 1656 | 274.4
ACSSAWTW | Pheasant/ACSS/AW/TW | 1272 | 39 | 19 |  | 0.0921 | 0.4605 | 1.264 |  | 13 | 3 | 25 | 0.0712 | 75 | 0.0866 | 1201 | 363.8
ACSSAWTW | Phoenix/ACSS/AW/TW | 954 | 30 | 7 |  | 0.0837 | 0.2511 | 1.044 |  | 5 | 3 | 25 | 0.0961 | 75 | 0.1175 | 897.7 | 110.5
ACSSAWTW | Platte/ACSS/AW/TW | 1569 | 33 | 7 |  | 0.1074 | 0.3222 | 1.334 |  | 5 | 3 | 25 | 0.0608 | 75 | 0.0733 | 1476 | 181.9
ACSSAWTW | Plover/ACSS/AW/TW | 1431 | 39 | 19 |  | 0.0977 | 0.4885 | 1.337 |  | 13 | 3 | 25 | 0.0638 | 75 | 0.0774 | 1351 | 409.4
ACSSAWTW | Potomac/ACSS/AW/TW | 1557.4 | 36 | 7 |  | 0.1241 | 0.3723 | 1.345 |  | 7 | 3 | 25 | 0.0606 | 75 | 0.0732 | 1467 | 242.9
ACSSAWTW | Powder/ACSS/AW/TW | 2153.8 | 64 | 19 |  | 0.0961 | 0.4805 | 1.602 |  | 8 | 4 | 25 | 0.0458 | 75 | 0.0536 | 2043 | 396.1
ACSSAWTW | Puffin/ACSS/AW/TW | 795 | 18 | 7 |  | 0.1108 | 0.3324 | 0.980 |  | 10 | 2 | 25 | 0.1116 | 75 | 0.1337 | 745.9 | 193.6
ACSSAWTW | Rail/ACSS/AW/TW | 954 | 32 | 7 |  | 0.0971 | 0.2913 | 1.061 |  | 7 | 3 | 25 | 0.0955 | 75 | 0.1168 | 898.6 | 148.7
ACSSAWTW | Rio Grande/ACSS/AW/TW | 1533.3 | 39 | 19 |  | 0.1012 | 0.506 | 1.382 |  | 13 | 3 | 25 | 0.0599 | 75 | 0.0725 | 1448 | 439.3
ACSSAWTW | Rook/ACSS/AW/TW | 636 | 18 | 7 |  | 0.1085 | 0.3255 | 0.890 |  | 13 | 2 | 25 | 0.1379 | 75 | 0.1654 | 597.0 | 185.7
ACSSAWTW | Santee/ACSS/AW/TW | 2627.3 | 64 | 19 |  | 0.1062 | 0.531 | 1.762 |  | 8 | 4 | 25 | 0.0391 | 75 | 0.0453 | 2492 | 483.8
ACSSAWTW | Schuylkill/ACSS/AW/TW | 1657.4 | 36 | 7 |  | 0.128 | 0.384 | 1.386 |  | 7 | 3 | 25 | 0.0574 | 75 | 0.0691 | 1561 | 258.4
ACSSAWTW | Scissortail/ACSS/AW/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0734 | 75 | 0.0891 | 1198 | 147.5
ACSSAWTW | Scoter/ACSS/AW/TW | 636 | 18 | 7 |  | 0.1456 | 0.4368 | 0.953 |  | 23 | 2 | 25 | 0.1334 | 75 | 0.1599 | 597.6 | 334.3
ACSSAWTW | Snowbird/ACSS/AW/TW | 1033.5 | 30 | 7 |  | 0.0871 | 0.2613 | 1.089 |  | 5 | 3 | 25 | 0.0891 | 75 | 0.1087 | 972.5 | 119.6
ACSSAWTW | St. Croix/ACSS/AW/TW | 1467.8 | 33 | 7 |  | 0.1041 | 0.3123 | 1.292 |  | 5 | 3 | 25 | 0.0645 | 75 | 0.0779 | 1381 | 170.9
ACSSAWTW | Suwannee/ACSS/AW/TW | 959.6 | 22 | 7 |  | 0.1493 | 0.4479 | 1.108 |  | 16 | 2 | 25 | 0.0913 | 75 | 0.1092 | 901.6 | 351.5
ACSSAWTW | Tern/ACSS/AW/TW | 795 | 17 | 7 |  | 0.0886 | 0.2658 | 0.960 |  | 7 | 2 | 25 | 0.1132 | 75 | 0.1355 | 745.2 | 123.8
ACSSAWTW | Thames/ACSS/AW/TW | 1334.6 | 39 | 19 |  | 0.0944 | 0.472 | 1.29 |  | 13 | 3 | 25 | 0.0680 | 75 | 0.0827 | 1260 | 382.2
ACSSAWTW | Truckee/ACSS/AW/TW | 1372.5 | 30 | 7 |  | 0.1004 | 0.3012 | 1.248 |  | 5 | 3 | 25 | 0.0685 | 75 | 0.0830 | 1292 | 159.0
ACSSAWTW | Wabash/ACSS/AW/TW | 762.8 | 20 | 7 |  | 0.1331 | 0.3993 | 0.99 |  | 16 | 2 | 25 | 0.1142 | 75 | 0.1368 | 716.7 | 279.4
ACSSAWTW | Yukon/ACSS/AW/TW | 1233.6 | 38 | 19 |  | 0.091 | 0.455 | 1.245 |  | 13 | 3 | 25 | 0.0732 | 75 | 0.0892 | 1166.5 | 355.2
ACSSTW | Athabaska/ACSS/TW | 1949.6 | 42 | 7 |  | 0.1392 | 0.4176 | 1.504 |  | 7 | 3 | 25 | 0.0505 | 75 | 0.0595 | 1836 | 361
ACSSTW | Avocet/ACSS/TW | 1113 | 30 | 7 |  | 0.0904 | 0.2712 | 1.129 |  | 5 | 3 | 25 | 0.0838 | 75 | 0.0938 | 1047 | 152.1
ACSSTW | Bittern/ACSS/TW | 1272 | 35 | 7 |  | 0.1121 | 0.3363 | 1.22 |  | 7 | 3 | 25 | 0.0737 | 75 | 0.0899 | 1198 | 233.9
ACSSTW | Bluebird/ACSS/TW | 2156 | 64 | 19 |  | 0.0961 | 0.4805 | 1.608 |  | 8 | 4 | 25 | 0.0464 | 75 | 0.0543 | 2045 | 467.5
ACSSTW | Bluejay/ACSS/TW | 1113 | 33 | 7 |  | 0.1049 | 0.3147 | 1.143 |  | 7 | 3 | 25 | 0.0835 | 75 | 0.0935 | 1048 | 204.8
ACSSTW | Bobolink/ACSS/TW | 1431 | 36 | 7 |  | 0.1189 | 0.3567 | 1.291 |  | 7 | 3 | 25 | 0.0662 | 75 | 0.0804 | 1347 | 263.1
ACSSTW | Bunting/ACSS/TW | 1192.5 | 33 | 7 |  | 0.1085 | 0.3255 | 1.181 |  | 7 | 3 | 25 | 0.0783 | 75 | 0.0956 | 1123 | 219.1
ACSSTW | Calumet/ACSS/TW | 565.3 | 20 | 7 |  | 0.1146 | 0.3441 | 0.858 |  | 16 | 2 | 25 | 0.1581 | 75 | 0.1898 | 531.2 | 244.4
ACSSTW | Canary/ACSS/TW | 900 | 20 | 7 |  | 0.1291 | 0.3873 | 1.055 |  | 13 | 3 | 25 | 0.1007 | 75 | 0.1205 | 844.9 | 310.2
ACSSTW | Cardinal/ACSS/TW | 954 | 20 | 7 |  | 0.1329 | 0.3987 | 1.084 |  | 13 | 2 | 25 | 0.0952 | 75 | 0.1138 | 895.5 | 328.7
ACSSTW | Catawba/ACSS/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0741 | 75 | 0.0902 | 1197 | 174
ACSSTW | Cheyenne/ACSS/TW | 1168.1 | 30 | 7 |  | 0.0926 | 0.2778 | 1.155 |  | 5 | 3 | 25 | 0.0801 | 75 | 0.0979 | 1099 | 159.6
ACSSTW | Chukar/ACSS/TW | 1780 | 37 | 19 |  | 0.0874 | 0.437 | 1.445 |  | 8 | 3 | 25 | 0.0542 | 75 | 0.0654 | 1675 | 386.7
ACSSTW | Columbia/ACSS/TW | 966.2 | 21 | 7 |  | 0.1338 | 0.4014 | 1.092 |  | 13 | 2 | 25 | 0.0940 | 75 | 0.1124 | 906.9 | 333.2
ACSSTW | Condor/ACSS/TW | 795 | 20 | 7 |  | 0.1213 | 0.3639 | 0.993 |  | 13 | 2 | 25 | 0.1136 | 75 | 0.1361 | 746.3 | 273.9
ACSSTW | Cumberland/ACSS/TW | 1926.9 | 42 | 19 |  | 0.1133 | 0.5665 | 1.545 |  | 13 | 3 | 25 | 0.0499 | 75 | 0.0602 | 1819 | 649.8
ACSSTW | Curlew/ACSS/TW | 1033.5 | 20 | 7 |  | 0.1383 | 0.4149 | 1.129 |  | 13 | 2 | 25 | 0.0881 | 75 | 0.1053 | 970.1 | 356.0
ACSSTW | Dipper/ACSS/TW | 1351.5 | 35 | 7 |  | 0.1155 | 0.3465 | 1.256 |  | 7 | 3 | 25 | 0.0697 | 75 | 0.0849 | 1273 | 248.3
ACSSTW | Dove/ACSS/TW | 556.5 | 20 | 7 |  | 0.1138 | 0.3414 | 0.852 |  | 16 | 2 | 25 | 0.1606 | 75 | 0.1928 | 522.9 | 241
ACSSTW | Drake/ACSS/TW | 795 | 20 | 7 |  | 0.136 | 0.408 | 1.010 |  | 16 | 2 | 25 | 0.1130 | 75 | 0.1355 | 747.0 | 344.2
ACSSTW | Falcon/ACSS/TW | 1590 | 42 | 19 |  | 0.103 | 0.515 | 1.408 |  | 13 | 3 | 25 | 0.0592 | 75 | 0.0719 | 1501 | 537
ACSSTW | Finch/ACSS/TW | 1113 | 38 | 19 |  | 0.0862 | 0.431 | 1.185 |  | 13 | 3 | 25 | 0.0826 | 75 | 0.1012 | 1051 | 376.1
ACSSTW | Flicker/ACSS/TW | 477 | 18 | 7 |  | 0.094 | 0.282 | 0.776 |  | 13 | 2 | 25 | 0.1877 | 75 | 0.2255 | 447.8 | 164.4
ACSSTW | Fraser/ACSS/TW | 946.7 | 35 | 7 |  | 0.1154 | 0.3462 | 1.077 |  | 10 | 3 | 25 | 0.0969 | 75 | 0.1190 | 892.6 | 248
ACSSTW | Genesee/ACSS/TW | 1158 | 33 | 7 |  | 0.1078 | 0.3234 | 1.165 |  | 7 | 3 | 25 | 0.0805 | 75 | 0.0983 | 1091 | 216
ACSSTW | Grackle/ACSS/TW | 1192.5 | 38 | 19 |  | 0.0892 | 0.446 | 1.225 |  | 13 | 3 | 25 | 0.0773 | 75 | 0.0947 | 1126 | 403
ACSSTW | Grosbeak/ACSS/TW | 636 | 20 | 7 |  | 0.1216 | 0.3648 | 0.908 |  | 16 | 2 | 25 | 0.1407 | 75 | 0.1689 | 597.6 | 275.1
ACSSTW | Hawk/ACSS/TW | 477 | 18 | 7 |  | 0.1053 | 0.3159 | 0.789 |  | 16 | 2 | 25 | 0.1870 | 75 | 0.2247 | 448.1 | 206.3
ACSSTW | Hen/ACSS/TW | 477 | 16 | 7 |  | 0.1261 | 0.3783 | 0.825 |  | 23 | 2 | 25 | 0.1852 | 75 | 0.2225 | 448.3 | 296
ACSSTW | Hudson/ACSS/TW | 1158.4 | 25 | 7 |  | 0.1467 | 0.4401 | 1.196 |  | 13 | 2 | 25 | 0.0790 | 75 | 0.0943 | 1087 | 400
ACSSTW | James/ACSS/TW | 1730.6 | 39 | 19 |  | 0.1075 | 0.5375 | 1.470 |  | 13 | 3 | 25 | 0.0549 | 75 | 0.0664 | 1634 | 585
ACSSTW | Kettle/ACSS/TW | 957.2 | 32 | 7 |  | 0.0973 | 0.2919 | 1.060 |  | 7 | 3 | 25 | 0.0964 | 75 | 0.1183 | 901.6 | 176.2
ACSSTW | Lapwing/ACSS/TW | 1590 | 36 | 7 |  | 0.1253 | 0.3759 | 1.358 |  | 7 | 3 | 25 | 0.0602 | 75 | 0.0729 | 1498 | 292
ACSSTW | Linnet/ACSS/TW | 336.4 | 18 | 7 |  | 0.0884 | 0.2652 | 0.659 |  | 16 | 2 | 25 | 0.2647 | 75 | 0.3181 | 315.9 | 145.5
ACSSTW | Mackenzie/ACSS/TW | 1359.7 | 36 | 7 |  | 0.1159 | 0.3477 | 1.259 |  | 7 | 3 | 25 | 0.0694 | 75 | 0.0844 | 1281 | 250
ACSSTW | Martin/ACSS/TW | 1351.5 | 39 | 19 |  | 0.0949 | 0.4745 | 1.300 |  | 13 | 3 | 25 | 0.0688 | 75 | 0.0839 | 1276 | 456
ACSSTW | Maumee/ACSS/TW | 768.2 | 20 | 7 |  | 0.1195 | 0.3585 | 0.977 |  | 13 | 2 | 25 | 0.1174 | 75 | 0.1407 | 721.1 | 265.7
ACSSTW | Merrimack/ACSS/TW | 1433.6 | 39 | 19 |  | 0.0978 | 0.489 | 1.340 |  | 13 | 3 | 25 | 0.0651 | 75 | 0.0793 | 1354 | 484.2
ACSSTW | MiramichiACSS/TW | 1455.3 | 36 | 7 |  | 0.120 | 0.360 | 1.302 |  | 7 | 3 | 25 | 0.0652 | 75 | 0.0792 | 1371 | 268
ACSSTW | Mohawk/ACSS/TW | 571.7 | 18 | 7 |  | 0.103 | 0.309 | 0.846 |  | 13 | 2 | 25 | 0.1570 | 75 | 0.1884 | 536.6 | 197.4
ACSSTW | Mystic/ACSS/TW | 666.6 | 20 | 7 |  | 0.1111 | 0.3333 | 0.913 |  | 13 | 2 | 25 | 0.1349 | 75 | 0.1619 | 625.7 | 229.7
ACSSTW | Nelson/ACSS/TW | 1257.1 | 35 | 7 |  | 0.1115 | 0.3345 | 1.213 |  | 7 | 3 | 25 | 0.0745 | 75 | 0.0909 | 1184 | 231.3
ACSSTW | Oriole/ACSS/TW | 336.4 | 16 | 7 |  | 0.1059 | 0.3177 | 0.693 |  | 23 | 2 | 25 | 0.2622 | 75 | 0.3151 | 316.1 | 208.7
ACSSTW | Ortolan/ACSS/TW | 1033.5 | 32 | 7 |  | 0.101 | 0.303 | 1.102 |  | 7 | 3 | 25 | 0.0896 | 75 | 0.1098 | 972.5 | 189.8
ACSSTW | Oswego/ACSS/TW | 664.8 | 20 | 7 |  | 0.1244 | 0.3732 | 0.927 |  | 16 | 2 | 25 | 0.1347 | 75 | 0.1617 | 624.6 | 288
ACSSTW | Oxbird/ACSS/TW | 1192.5 | 30 | 7 |  | 0.0936 | 0.2808 | 1.167 |  | 5 | 3 | 25 | 0.0786 | 75 | 0.0960 | 1122 | 163
ACSSTW | Parakeet/ACSS/TW | 556.5 | 18 | 7 |  | 0.1015 | 0.3045 | 0.835 |  | 13 | 2 | 25 | 0.1612 | 75 | 0.1935 | 522.4 | 191.7
ACSSTW | Pecos/ACSS/TW | 1622 | 39 | 19 |  | 0.1064 | 0.532 | 1.424 |  | 13 | 3 | 25 | 0.0580 | 75 | 0.0705 | 1532 | 574
ACSSTW | Pee Dee/ACSS/TW | 1758.6 | 37 | 7 |  | 0.1319 | 0.3957 | 1.427 |  | 7 | 3 | 25 | 0.0551 | 75 | 0.0665 | 1656 | 324
ACSSTW | Pheasant/ACSS/TW | 1272 | 39 | 19 |  | 0.0921 | 0.4605 | 1.264 |  | 13 | 3 | 25 | 0.0728 | 75 | 0.0890 | 1201 | 430
ACSSTW | Phoenix/ACSS/TW | 954 | 30 | 7 |  | 0.0837 | 0.2511 | 1.044 |  | 5 | 3 | 25 | 0.0970 | 75 | 0.1190 | 897.7 | 130.4
ACSSTW | Platte/ACSS/TW | 1569 | 33 | 7 |  | 0.1074 | 0.3222 | 1.334 |  | 5 | 3 | 25 | 0.0613 | 75 | 0.0742 | 1476 | 215
ACSSTW | Plover/ACSS/TW | 1431 | 39 | 19 |  | 0.0977 | 0.4885 | 1.337 |  | 13 | 3 | 25 | 0.0652 | 75 | 0.0795 | 1351 | 483
ACSSTW | Potomac/ACSS/TW | 1557.4 | 36 | 7 |  | 0.1241 | 0.3723 | 1.345 |  | 7 | 3 | 25 | 0.0613 | 75 | 0.0743 | 1467 | 287
ACSSTW | Powder/ACSS/TW | 2153.8 | 64 | 19 |  | 0.0961 | 0.4805 | 1.602 |  | 8 | 4 | 25 | 0.0464 | 75 | 0.0543 | 2043 | 467.5
ACSSTW | Puffin/ACSS/TW | 795 | 18 | 7 |  | 0.1108 | 0.3324 | 0.980 |  | 10 | 2 | 25 | 0.1139 | 75 | 0.1365 | 745.9 | 228.4
ACSSTW | Rail/ACSS/TW | 954 | 32 | 7 |  | 0.0971 | 0.2913 | 1.061 |  | 7 | 3 | 25 | 0.0967 | 75 | 0.1187 | 898.6 | 175
ACSSTW | Rio Grande/ACSS/TW | 1533.3 | 39 | 19 |  | 0.1012 | 0.506 | 1.382 |  | 13 | 3 | 25 | 0.0612 | 75 | 0.0744 | 1448 | 519
ACSSTW | Rook/ACSS/TW | 636 | 18 | 7 |  | 0.1085 | 0.3255 | 0.890 |  | 13 | 2 | 25 | 0.1413 | 75 | 0.1696 | 597.0 | 219.1
ACSSTW | Santee/ACSS/TW | 2627.3 | 64 | 19 |  | 0.1062 | 0.531 | 1.762 |  | 8 | 4 | 25 | 0.0396 | 75 | 0.0459 | 2492 | 571
ACSSTW | Schuylkill/ACSS/TW | 1657.4 | 36 | 7 |  | 0.128 | 0.384 | 1.386 |  | 7 | 3 | 25 | 0.0581 | 75 | 0.0702 | 1561 | 305
ACSSTW | Scissortail/ACSS/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0741 | 75 | 0.0902 | 1198 | 174
ACSSTW | Scoter/ACSS/TW | 636 | 18 | 7 |  | 0.1456 | 0.4368 | 0.953 |  | 23 | 2 | 25 | 0.1393 | 75 | 0.1672 | 597.6 | 394.6
ACSSTW | Snowbird/ACSS/TW | 1033.5 | 30 | 7 |  | 0.0871 | 0.2613 | 1.089 |  | 5 | 3 | 25 | 0.0899 | 75 | 0.1101 | 972.5 | 141.2
ACSSTW | St. Croix/ACSS/TW | 1467.8 | 33 | 7 |  | 0.1041 | 0.3123 | 1.292 |  | 5 | 3 | 25 | 0.0650 | 75 | 0.0789 | 1381 | 202
ACSSTW | Suwannee/ACSS/TW | 959.6 | 22 | 7 |  | 0.1493 | 0.4479 | 1.108 |  | 16 | 2 | 25 | 0.0941 | 75 | 0.1127 | 901.6 | 415
ACSSTW | Tern/ACSS/TW | 795 | 17 | 7 |  | 0.0886 | 0.2658 | 0.960 |  | 7 | 2 | 25 | 0.1147 | 75 | 0.1373 | 745.2 | 146.1
ACSSTW | Thames/ACSS/TW | 1334.6 | 39 | 19 |  | 0.0944 | 0.472 | 1.29 |  | 13 | 3 | 25 | 0.0696 | 75 | 0.0849 | 1260 | 451.4
ACSSTW | Truckee/ACSS/TW | 1372.5 | 30 | 7 |  | 0.1004 | 0.3012 | 1.248 |  | 5 | 3 | 25 | 0.0691 | 75 | 0.0840 | 1292 | 187.6
ACSSTW | Wabash/ACSS/TW | 762.8 | 20 | 7 |  | 0.1331 | 0.3993 | 0.99 |  | 16 | 2 | 25 | 0.1177 | 75 | 0.1411 | 716.7 | 330
ACSSTW | Yukon/ACSS/TW | 1233.6 | 38 | 19 |  | 0.091 | 0.455 | 1.245 |  | 13 | 3 | 25 | 0.0749 | 75 | 0.0916 | 1166.5 | 419.5
Alumoweld | 37 No. 5 | 1225 | 37 |  | 0.1819 |  |  | 1.270 |  |  |  | 25 | 0.2327 | 75 | 0.4788 | 2802
Alumoweld | 37 No. 6 | 971.3 | 37 |  | 0.162 |  |  | 1.130 |  |  |  | 25 | 0.2935 | 75 | 0.5546 | 2222
Alumoweld | 37 No. 7 | 770.3 | 37 |  | 0.1443 |  |  | 1.010 |  |  |  | 25 | 0.3702 | 75 | 0.6524 | 1762
Alumoweld | 37 No. 8 | 610.9 | 37 |  | 0.1285 |  |  | 0.899 |  |  |  | 25 | 0.4667 | 75 | 0.7679 | 1398
Alumoweld | 37 No. 9 | 484.4 | 37 |  | 0.1144 |  |  | 0.801 |  |  |  | 25 | 0.5886 | 75 | 0.9144 | 1108
Alumoweld | 37 No. 10 | 384.2 | 37 |  | 0.1019 |  |  | 0.713 |  |  |  | 25 | 0.7409 | 75 | 1.093 | 879
Alumoweld | 19 No. 5 | 628.9 | 19 |  | 0.1819 |  |  | 0.910 |  |  |  | 25 | 0.4507 | 75 | 0.7585 | 1430
Alumoweld | 19 No. 6 | 498.8 | 19 |  | 0.162 |  |  | 0.810 |  |  |  | 25 | 0.5683 | 75 | 0.8886 | 1134
Alumoweld | 19 No. 7 | 395.5 | 19 |  | 0.1443 |  |  | 0.721 |  |  |  | 25 | 0.7171 | 75 | 1.064 | 899.5
Alumoweld | 19 No. 8 | 313.7 | 19 |  | 0.1285 |  |  | 0.642 |  |  |  | 25 | 0.9038 | 75 | 1.28 | 713.5
Alumoweld | 19 No. 9 | 248.8 | 19 |  | 0.1144 |  |  | 0.572 |  |  |  | 25 | 1.14 | 75 | 1.554 | 565.8
Alumoweld | 19 No. 10 | 197.3 | 19 |  | 0.1019 |  |  | 0.509 |  |  |  | 25 | 1.437 | 75 | 1.896 | 448.7
Alumoweld | 7 No. 5 | 231.7 | 7 |  | 0.1819 |  |  | 0.546 |  |  |  | 25 | 1.24 | 75 | 1.669 | 524.9
Alumoweld | 7 No. 6 | 183.8 | 7 |  | 0.162 |  |  | 0.486 |  |  |  | 25 | 1.536 | 75 | 2.01 | 416.3
Alumoweld | 7 No. 7 | 145.7 | 7 |  | 0.1443 |  |  | 0.433 |  |  |  | 25 | 1.937 | 75 | 2.47 | 330
Alumoweld | 7 No. 8 | 115.6 | 7 |  | 0.1285 |  |  | 0.385 |  |  |  | 25 | 2.44 | 75 | 3.06 | 261.8
Alumoweld | 7 No. 9 | 91.65 | 7 |  | 0.1144 |  |  | 0.343 |  |  |  | 25 | 3.08 | 75 | 3.8 | 207.6
Alumoweld | 7 No. 10 | 72.68 | 7 |  | 0.1019 |  |  | 0.306 |  |  |  | 25 | 3.88 | 75 | 4.73 | 164.7
Alumoweld | 3 No. 5 | 99.31 | 3 |  | 0.1819 |  |  | 0.392 |  |  |  | 25 | 2.78 | 75 | 3.56 | 224.5
Alumoweld | 3 No. 6 | 78.75 | 3 |  | 0.162 |  |  | 0.349 |  |  |  | 25 | 3.51 | 75 | 4.41 | 178.1
Alumoweld | 3 No. 7 | 62.45 | 3 |  | 0.1443 |  |  | 0.311 |  |  |  | 25 | 4.42 | 75 | 5.47 | 141.2
Alumoweld | 3 No. 8 | 49.53 | 3 |  | 0.1285 |  |  | 0.277 |  |  |  | 25 | 5.58 | 75 | 6.82 | 112
Alumoweld | 3 No. 9 | 39.28 | 3 |  | 0.1144 |  |  | 0.247 |  |  |  | 25 | 7.04 | 75 | 8.52 | 88.8
Alumoweld | 3 No. 10 | 31.15 | 3 |  | 0.1019 |  |  | 0.220 |  |  |  | 25 | 8.87 | 75 | 10.67 | 70.4
HDCopper | 1 - 1 | 1 | 1 |  | 0.2893 |  |  | 0.2893 |  |  |  | 25 | 0.6938 | 75 | 0.8226 | 253.3
HDCopper | 1 - 3 | 1 | 3 |  | 0.167 |  |  | 0.359885 |  |  |  | 25 | 0.7007 | 75 | 0.8309 | 255.9
HDCopper | 1 - 7 | 1 | 7 |  | 0.1093 |  |  | 0.3279 |  |  |  | 25 | 0.7076 | 75 | 0.8391 | 258.4
HDCopper | 1/0 - 1 | 1/0 | 1 |  | 0.3249 |  |  | 0.3249 |  |  |  | 25 | 0.5500 | 75 | 0.6521 | 319.5
HDCopper | 1/0 - 19 | 1/0 | 19 |  | 0.0745 |  |  | 0.3725 |  |  |  | 25 | 0.5610 | 75 | 0.6652 | 325.595758815
HDCopper | 1/0 - 7 | 1/0 | 7 |  | 0.1228 |  |  | 0.3684 |  |  |  | 25 | 0.5610 | 75 | 0.6652 | 325.9172643552
HDCopper | 1000 - 37 | 1000 | 37 |  | 0.1644 |  |  | 1.1508 |  |  |  | 25 | 0.0642 | 75 | 0.0745 | 3087.5780384928
HDCopper | 1000 - 61 | 1000 | 61 |  | 0.128 |  |  | 1.152 |  |  |  | 25 | 0.0642 | 75 | 0.0745 | 3085.76157696
HDCopper | 1250 - 61 | 1250 | 61 |  | 0.1431 |  |  | 1.288 |  |  |  | 25 | 0.0533 | 75 | 0.0613 | 3859
HDCopper | 1500 - 61 | 1500 | 61 |  | 0.1568 |  |  | 1.411 |  |  |  | 25 | 0.0463 | 75 | 0.0528 | 4631
HDCopper | 1750 - 91 | 1750 | 91 |  | 0.1387 |  |  | 1.526 |  |  |  | 25 | 0.0415 | 75 | 0.0469 | 5403
HDCopper | 2 - 1 | 2 | 1 |  | 0.2576 |  |  | 0.2576 |  |  |  | 25 | 0.8747 | 75 | 1.0373 | 200.9
HDCopper | 2 - 3 | 2 | 3 |  | 0.1487 |  |  | 0.3204485 |  |  |  | 25 | 0.8835 | 75 | 1.0477 | 202.9
HDCopper | 2 - 7 | 2 | 7 |  | 0.0974 |  |  | 0.2922 |  |  |  | 25 | 0.8922 | 75 | 1.0580 | 204.9
HDCopper | 2/0 - 1 | 2/0 | 1 |  | 0.3648 |  |  | 0.3648 |  |  |  | 25 | 0.4322 | 75 | 0.5130 | 402.6
HDCopper | 2/0 - 19 | 2/0 | 19 |  | 0.0837 |  |  | 0.4185 |  |  |  | 25 | 0.4454 | 75 | 0.5280 | 410.9766139494
HDCopper | 2/0 - 7 | 2/0 | 7 |  | 0.1379 |  |  | 0.4137 |  |  |  | 25 | 0.4454 | 75 | 0.5280 | 410.9974857198
HDCopper | 2000 - 91 | 2000 | 91 |  | 0.1482 |  |  | 1.63 |  |  |  | 25 | 0.0379 | 75 | 0.0426 | 6175
HDCopper | 250 - 12 | 250 | 12 |  | 0.1443 |  |  | 0.5995665 |  |  |  | 25 | 0.2381 | 75 | 0.2819 | 771.4832492952
HDCopper | 250 - 19 | 250 | 19 |  | 0.1147 |  |  | 0.5735 |  |  |  | 25 | 0.2381 | 75 | 0.2819 | 771.7791282534
HDCopper | 250 - 37 | 250 | 37 |  | 0.0822 |  |  | 0.5754 |  |  |  | 25 | 0.2381 | 75 | 0.2819 | 771.8945096232
HDCopper | 3 - 1 | 3 | 1 |  | 0.2294 |  |  | 0.2294 |  |  |  | 25 | 1.1030 | 75 | 1.3080 | 159.3
HDCopper | 3 - 3 | 3 | 3 |  | 0.1325 |  |  | 0.2855375 |  |  |  | 25 | 1.1140 | 75 | 1.3211 | 160.9
HDCopper | 3 - 7 | 3 | 7 |  | 0.0867 |  |  | 0.2601 |  |  |  | 25 | 1.1250 | 75 | 1.3342 | 162.4608898542
HDCopper | 3/0 - 1 | 3/0 | 1 |  | 0.4096 |  |  | 0.4096 |  |  |  | 25 | 0.3432 | 75 | 0.4072 | 507.8
HDCopper | 3/0 - 12 | 3/0 | 12 |  | 0.1183 |  |  | 0.4915365 |  |  |  | 25 | 0.3536 | 75 | 0.4191 | 518.5173920472
HDCopper | 3/0 - 19 | 3/0 | 19 |  | 0.0904 |  |  | 0.452 |  |  |  | 25 | 0.3536 | 75 | 0.4191 | 518.3
HDCopper | 3/0 - 7 | 3/0 | 7 |  | 0.1548 |  |  | 0.4644 |  |  |  | 25 | 0.3536 | 75 | 0.4191 | 517.9079116512
HDCopper | 300 - 12 | 300 | 12 |  | 0.1581 |  |  | 0.6569055 |  |  |  | 25 | 0.1989 | 75 | 0.2353 | 926.0993483928
HDCopper | 300 - 19 | 300 | 19 |  | 0.1257 |  |  | 0.6285 |  |  |  | 25 | 0.1989 | 75 | 0.2353 | 926.9082529974
HDCopper | 300 - 37 | 300 | 37 |  | 0.09 |  |  | 0.63 |  |  |  | 25 | 0.1989 | 75 | 0.2353 | 925.335738
HDCopper | 350 - 12 | 350 | 12 |  | 0.1708 |  |  | 0.709674 |  |  |  | 25 | 0.1709 | 75 | 0.2021 | 1080.8603148672
HDCopper | 350 - 19 | 350 | 19 |  | 0.1357 |  |  | 0.6785 |  |  |  | 25 | 0.1709 | 75 | 0.2021 | 1080.2540146374
HDCopper | 350 - 37 | 350 | 37 |  | 0.0973 |  |  | 0.6811 |  |  |  | 25 | 0.1709 | 75 | 0.2021 | 1081.5335529642
HDCopper | 4 - 1 | 4 | 1 |  | 0.2043 |  |  | 0.2043 |  |  |  | 25 | 1.3904 | 75 | 1.6488 | 126.3
HDCopper | 4 - 3 | 4 | 3 |  | 0.118 |  |  | 0.25429 |  |  |  | 25 | 1.4043 | 75 | 1.6653 | 127.6
HDCopper | 4 - 7 | 4 | 7 |  | 0.0772 |  |  | 0.2316 |  |  |  | 25 | 1.4182 | 75 | 1.6818 | 128.9
HDCopper | 4/0 - 1 | 4/0 | 1 |  | 0.46 |  |  | 0.46 |  |  |  | 25 | 0.2726 | 75 | 0.3233 | 640.5
HDCopper | 4/0 - 12 | 4/0 | 12 |  | 0.1328 |  |  | 0.551784 |  |  |  | 25 | 0.2808 | 75 | 0.3327 | 653.4163372032
HDCopper | 4/0 - 19 | 4/0 | 19 |  | 0.1055 |  |  | 0.5275 |  |  |  | 25 | 0.2808 | 75 | 0.3327 | 652.936749615
HDCopper | 4/0 - 7 | 4/0 | 7 |  | 0.1739 |  |  | 0.5217 |  |  |  | 25 | 0.2808 | 75 | 0.3327 | 653.5966186638
HDCopper | 400 - 19 | 400 | 19 |  | 0.1451 |  |  | 0.7255 |  |  |  | 25 | 0.1501 | 75 | 0.1773 | 1235.0968626726
HDCopper | 400 - 37 | 400 | 37 |  | 0.104 |  |  | 0.728 |  |  |  | 25 | 0.1501 | 75 | 0.1773 | 1235.60880768
HDCopper | 450 - 19 | 450 | 19 |  | 0.1539 |  |  | 0.7695 |  |  |  | 25 | 0.1339 | 75 | 0.1580 | 1389.4516323846
HDCopper | 450 - 37 | 450 | 37 |  | 0.1103 |  |  | 0.7721 |  |  |  | 25 | 0.1339 | 75 | 0.1580 | 1389.8417121882
HDCopper | 5 - 1 | 5 | 1 |  | 0.1819 |  |  | 0.1819 |  |  |  | 25 | 1.7537 | 75 | 2.0798 | 100.2
HDCopper | 500 - 19 | 500 | 19 |  | 0.1622 |  |  | 0.811 |  |  |  | 25 | 0.1210 | 75 | 0.1426 | 1543.3623212184
HDCopper | 500 - 37 | 500 | 37 |  | 0.1162 |  |  | 0.8134 |  |  |  | 25 | 0.1210 | 75 | 0.1426 | 1542.5049731112
HDCopper | 6 - 1 | 6 | 1 |  | 0.162 |  |  | 0.162 |  |  |  | 25 | 2.2114 | 75 | 2.6226 | 79.44
HDCopper | 6 - 7 | 6 | 7 |  | 0.0612 |  |  | 0.1836 |  |  |  | 25 | 2.2556 | 75 | 2.6751 | 81
HDCopper | 600 - 37 | 600 | 37 |  | 0.1273 |  |  | 0.8911 |  |  |  | 25 | 0.1018 | 75 | 0.1196 | 1851.2758002042
HDCopper | 600 - 61 | 600 | 61 |  | 0.0992 |  |  | 0.8928 |  |  |  | 25 | 0.1018 | 75 | 0.1196 | 1853.3855471616
HDCopper | 7 - 1 | 7 | 1 |  | 0.1443 |  |  | 0.1443 |  |  |  | 25 | 2.7870 | 75 | 3.3053 | 63.03
HDCopper | 700 - 37 | 700 | 37 |  | 0.1375 |  |  | 0.9625 |  |  |  | 25 | 0.0881 | 75 | 0.1033 | 2159.830715625
HDCopper | 700 - 61 | 700 | 61 |  | 0.1071 |  |  | 0.9639 |  |  |  | 25 | 0.0881 | 75 | 0.1033 | 2160.3363311754
HDCopper | 750 - 37 | 750 | 37 |  | 0.1424 |  |  | 0.9968 |  |  |  | 25 | 0.0827 | 75 | 0.0969 | 2316.5106190848
HDCopper | 750 - 61 | 750 | 61 |  | 0.1109 |  |  | 0.9981 |  |  |  | 25 | 0.0827 | 75 | 0.0969 | 2316.3571374714
HDCopper | 8 - 1 | 8 | 1 |  | 0.1285 |  |  | 0.1285 |  |  |  | 25 | 3.5146 | 75 | 4.1682 | 49.98
HDCopper | 800 - 37 | 800 | 37 |  | 0.147 |  |  | 1.029 |  |  |  | 25 | 0.0781 | 75 | 0.0912 | 2468.59011882
HDCopper | 800 - 61 | 800 | 61 |  | 0.1145 |  |  | 1.0305 |  |  |  | 25 | 0.0781 | 75 | 0.0912 | 2469.183698385
HDCopper | 900 - 37 | 900 | 37 |  | 0.156 |  |  | 1.092 |  |  |  | 25 | 0.0703 | 75 | 0.0819 | 2780.11981728
HDCopper | 900 - 61 | 900 | 61 |  | 0.1215 |  |  | 1.0935 |  |  |  | 25 | 0.0703 | 75 | 0.0819 | 2780.321279265
Paste Errors
Paste Errors
Paste Errors
Paste Errors
Paste Errors
Paste Errors
Paste Errors
VR2AAC | Cockscomb/VR2 (2 x 900-37) | 1800 | 37 |  | 0.156 |  |  | 1.638 |  |  |  | 25 | 0.0573 | 75 | 0.0667 | 1688
VR2AAC | Marigold/VR2 (2 x 1113-61) | 2226 | 61 |  | 0.1351 |  |  | 1.824 |  |  |  | 25 | 0.0488 | 75 | 0.0563 | 2087
VR2AAC | Camellia/VR2 (2 x 1000-61) | 2000 | 61 |  | 0.128 |  |  | 1.728 |  |  |  | 25 | 0.0526 | 75 | 0.0610 | 1874
VR2AAC | Larkspur/VR2 (2 x 1033.5-61) | 2067 | 61 |  | 0.1302 |  |  | 1.758 |  |  |  | 25 | 0.0517 | 75 | 0.0598 | 1939
VR2AAC | Lilac/VR2 (2 x 795-61) | 1590 | 61 |  | 0.1142 |  |  | 1.542 |  |  |  | 25 | 0.0636 | 75 | 0.0744 | 1491
VR2AAC | Bluebell/VR2 (2 x 1033.5-37) | 2067 | 37 |  | 0.1671 |  |  | 1.755 |  |  |  | 25 | 0.0517 | 75 | 0.0598 | 1937
VR2AAC | Goldenrod/VR2 (2 x 954-61) | 1908 | 61 |  | 0.1251 |  |  | 1.689 |  |  |  | 25 | 0.0546 | 75 | 0.0635 | 1790
VR2AAC | Magnolia/VR2 (2 x 954-37) | 1908 | 37 |  | 0.1606 |  |  | 1.686 |  |  |  | 25 | 0.0546 | 75 | 0.0635 | 1789
VR2AAC | Rose/VR2 (2 x #4) | 83.5 | 7 |  | 0.0772 |  |  | 0.348 |  |  |  | 25 | 1.1153 | 75 | 1.3361 | 78.30
VR2AAC | Lily/VR2 (2 x #3) | 105.2 | 7 |  | 0.0867 |  |  | 0.39 |  |  |  | 25 | 0.8854 | 75 | 1.0606 | 98.70
VR2AAC | Iris/VR2 (2 x #2) | 132.7 | 7 |  | 0.0974 |  |  | 0.438 |  |  |  | 25 | 0.7021 | 75 | 0.8409 | 124.5
VR2AAC | Pansy/VR2 (2 x #1) | 167.4 | 7 |  | 0.1093 |  |  | 0.492 |  |  |  | 25 | 0.5568 | 75 | 0.6668 | 156.9
VR2AAC | Poppy/VR2 (2 x #1/0) | 211.2 | 7 |  | 0.1228 |  |  | 0.552 |  |  |  | 25 | 0.4416 | 75 | 0.5287 | 198.1
VR2AAC | Aster/VR2 (2 x #2/0) | 266.2 | 7 |  | 0.1379 |  |  | 0.621 |  |  |  | 25 | 0.3507 | 75 | 0.4198 | 249.8
VR2AAC | Phlox/VR2 (2 x #3/0) | 335.6 | 7 |  | 0.1548 |  |  | 0.696 |  |  |  | 25 | 0.2786 | 75 | 0.3333 | 314.8
VR2AAC | Oxlip/VR2 (2 x #4/0) | 423.2 | 7 |  | 0.1739 |  |  | 0.783 |  |  |  | 25 | 0.2214 | 75 | 0.2648 | 397.2
VR2AAC | Daisy/VR2 (2 x 266.8) | 533.6 | 7 |  | 0.1953 |  |  | 0.879 |  |  |  | 25 | 0.1763 | 75 | 0.2105 | 501.0
VR2AAC | Laurel/VR2 (2 x 266.8-19) | 533.6 | 19 |  | 0.1185 |  |  | 0.8895 |  |  |  | 25 | 0.1763 | 75 | 0.2105 | 500.1
VR2AAC | Tulip/VR2 (2 x 336.4) | 672.8 | 19 |  | 0.1331 |  |  | 0.999 |  |  |  | 25 | 0.1406 | 75 | 0.1677 | 631.6
VR2AAC | Daffofil/VR2 (2 x 350-19) | 700 | 19 |  | 0.1357 |  |  | 1.0185 |  |  |  | 25 | 0.1353 | 75 | 0.1613 | 655.9
VR2AAC | Canna/VR2 (2 x 397.5) | 795 | 19 |  | 0.1447 |  |  | 1.086 |  |  |  | 25 | 0.1198 | 75 | 0.1425 | 746.5
VR2AAC | Cosmos/VR2 (2 x 477.0) | 954 | 19 |  | 0.1584 |  |  | 1.1895 |  |  |  | 25 | 0.1007 | 75 | 0.1196 | 894.6
VR2AAC | Syringa/VR2 (2 x 477-37) | 954 | 37 |  | 0.1135 |  |  | 1.1925 |  |  |  | 25 | 0.1007 | 75 | 0.1196 | 893.5
VR2AAC | Zinnia/VR2 (2 x 500-19) | 1000 | 19 |  | 0.1622 |  |  | 1.2165 |  |  |  | 25 | 0.0964 | 75 | 0.1143 | 937
VR2AAC | Hyacinth/VR2 (2 x 500-37) | 1000 | 37 |  | 0.1622 |  |  | 1.2195 |  |  |  | 25 | 0.0964 | 75 | 0.1143 | 936.5
VR2AAC | Dahlia/VR2 (2 x 556.5) | 1113 | 19 |  | 0.1711 |  |  | 1.284 |  |  |  | 25 | 0.0873 | 75 | 0.1033 | 1044
VR2AAC | Mistletoe/VR2 (2 x 556.5-37) | 1113 | 37 |  | 0.1226 |  |  | 1.287 |  |  |  | 25 | 0.0873 | 75 | 0.1033 | 1043
VR2AAC | Meadowsweet/VR2 (2 x 600-37) | 1200 | 37 |  | 0.1273 |  |  | 1.3365 |  |  |  | 25 | 0.0815 | 75 | 0.0962 | 1124
VR2AAC | Orchid/VR2 (2 x 636-37) | 1272 | 37 |  | 0.1311 |  |  | 1.377 |  |  |  | 25 | 0.0773 | 75 | 0.0912 | 1192
VR2AAC | Violet/VR2 (2 x 715.5-37) | 1431 | 37 |  | 0.1391 |  |  | 1.461 |  |  |  | 25 | 0.0696 | 75 | 0.0818 | 1342
VR2AAC | Nasturtium/VR2 (2 x 715.5-61) | 1431 | 61 |  | 0.1083 |  |  | 1.4625 |  |  |  | 25 | 0.0696 | 75 | 0.0818 | 1341
VR2AAC | Petunia/VR2 (2 x 750-37) | 1500 | 37 |  | 0.1424 |  |  | 1.4955 |  |  |  | 25 | 0.0668 | 75 | 0.0784 | 1407
VR2AAC | Arbutus/VR2 (2 x 795-37) | 1590 | 37 |  | 0.1466 |  |  | 1.539 |  |  |  | 25 | 0.0636 | 75 | 0.0744 | 1491
VR2ACSR | Cardinal/VR2 | 1908 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.794 |  |  |  | 25 | 0.0530 | 75 | 0.0633 | 1797 | 657
VR2ACSR | Bittern/VR2 | 2544 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 2.206 |  |  |  | 25 | 0.0379 | 75 | 0.0452
VR2ACSR | Swan/VR2 | 83.5 | 6 | 1 | 0.0834 | 0.0834 | 0.0834 | 0.375 | 3.35 |  |  | 25 | 1.0976 | 75 | 1.3884 | 78.30 | 36.80
VR2ACSR | Swallow/VR2 | 105.2 | 6 | 1 | 0.0937 | 0.0937 | 0.0937 | 0.4215 | 5.98 |  |  | 25 | 0.8713 | 75 | 1.0978 | 98.40 | 46.60
VR2ACSR | Sparrow/VR2 | 132.7 | 6 | 1 | 0.1052 | 0.1052 | 0.1052 | 0.474 | 4.23 |  |  | 25 | 0.6909 | 75 | 0.9007 | 124.0 | 58.70
VR2ACSR | Robin/VR2 | 167.4 | 6 | 1 | 0.1181 | 0.1182 | 0.1182 | 0.5325 | 4.75 |  |  | 25 | 0.5478 | 75 | 0.7292 | 156.3 | 73.90
VR2ACSR | Raven/VR2 | 211.2 | 6 | 1 | 0.1327 | 0.1327 | 0.1327 | 0.597 | 5.33 |  |  | 25 | 0.4344 | 75 | 0.5937 | 197.3 | 93.40
VR2ACSR | Quail/VR2 | 266.2 | 6 | 1 | 0.1489 | 0.1489 | 0.1489 | 0.6705 | 5.99 |  |  | 25 | 0.3450 | 75 | 0.4879 | 248.4 | 117.5
VR2ACSR | Pigeon/VR2 | 335.6 | 6 | 1 | 0.1672 | 0.1672 | 0.1672 | 0.753 | 6.72 |  |  | 25 | 0.2740 | 75 | 0.4036 | 313.2 | 148.2
VR2ACSR | Penguin/VR2 | 423.2 | 6 | 1 | 0.1878 | 0.1878 | 0.1878 | 0.8445 | 7.55 |  |  | 25 | 0.2177 | 75 | 0.3349 | 395.1 | 187.0
VR2ACSR | Jaeger/VR2 | 456.4 | 18 | 1 | 0.1126 | 0.1126 | 0.1126 | 0.8445 | 10.14 |  |  | 25 | 0.2046 | 75 | 0.2446 | 428.2 | 67.20
VR2ACSR | Waxwing/VR2 | 672.8 | 6 | 7 | 0.1217 | 0.1217 | 0.1217 | 0.9135 |  |  |  | 25 | 0.1725 | 75 | 0.2059 | 500.3 | 78.50
VR2ACSR | Partridge/VR2 | 533.6 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.963 |  |  |  | 25 | 0.1748 | 75 | 0.2089 | 503.1 | 231.4
VR2ACSR | Merlin/VR2 | 672.8 | 18 | 1 | 0.1367 | 0.1367 | 0.1367 | 1.026 |  |  |  | 25 | 0.1399 | 75 | 0.1669 | 631.2 | 99.10
VR2ACSR | Linnet/VR2 | 672.8 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 1.08 |  |  |  | 25 | 0.1393 | 75 | 0.1662 | 633.8 | 291.2
VR2ACSR | Oriole/VR2 | 672.8 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 1.1115 |  |  |  | 25 | 0.1368 | 75 | 0.1631 | 635 | 418
VR2ACSR | Chickadee/VR2 | 795 | 18 | 1 | 0.1486 | 0.1486 | 0.1486 | 1.1145 |  |  |  | 25 | 0.1191 | 75 | 0.1418 | 745.9 | 117.1
VR2ACSR | Brant/VR2 | 795 | 24 | 7 | 0.1287 | 0.0858 | 0.2547 | 1.158 |  |  |  | 25 | 0.1178 | 75 | 0.1403 | 749 | 274
VR2ACSR | Ptarmigan/VR2 | 795 | 20 | 7 | 0.141 | 0.0627 | 0.1881 | 1.128 |  |  |  | 25 | 0.1194 | 75 | 0.1422 | 749.0 | 146.4
VR2ACSR | Ibis/VR2 | 795 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 1.1745 |  |  |  | 25 | 0.1184 | 75 | 0.1411 | 749.0 | 334.1
VR2ACSR | Lark/VR2 | 795 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 1.209 |  |  |  | 25 | 0.1163 | 75 | 0.1385 | 751 | 493
VR2ACSR | Pelican/VR2 | 954 | 18 | 1 | 0.1628 | 0.1628 | 0.1628 | 1.221 |  |  |  | 25 | 0.1001 | 75 | 0.1189 | 895.2 | 140.5
VR2ACSR | Tailorbird/VR2 | 954 | 20 | 7 | 0.1544 | 0.0686 | 0.2058 | 1.236 |  |  |  | 25 | 0.1003 | 75 | 0.1192 | 899.1 | 175.3
VR2ACSR | Flicker/VR2 | 954 | 24 | 7 | 0.141 | 0.094 | 0.282 | 1.269 |  |  |  | 25 | 0.0997 | 75 | 0.1185 | 898.8 | 329.2
VR2ACSR | Hawk/VR2 | 954 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 1.287 |  |  |  | 25 | 0.0994 | 75 | 0.1182 | 898.8 | 413.1
VR2ACSR | Hen/VR2 | 954 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 1.3245 |  |  |  | 25 | 0.0990 | 75 | 0.1178 | 901.7 | 592.5
VR2ACSR | Nightingale/VR2 | 1033.5 | 18 | 1 | 0.1694 | 0.1694 | 0.1694 | 1.2705 | 15.25 |  |  | 25 | 0.0930 | 75 | 0.1104 | 973.9 | 189.9
VR2ACSR | Creeper/VR2 | 1033.5 | 20 | 7 | 0.1607 | 0.0714 | 0.2142 | 1.2855 |  |  |  | 25 | 0.0928 | 75 | 0.1101 | 969.3 | 152.1
VR2ACSR | Osprey/VR2 | 1113 | 18 | 1 | 0.1758 | 0.1758 | 0.1758 | 1.3185 | 9.669 |  |  | 25 | 0.0866 | 75 | 0.1026 | 1044 | 163.8
VR2ACSR | Tody/VR2 | 1113 | 20 | 7 | 0.1668 | 0.0741 | 0.2223 | 1.335 |  |  |  | 25 | 0.0868 | 75 | 0.1029 | 1048 | 204.6
VR2ACSR | Parakeet/VR2 | 1113 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 1.371 |  |  |  | 25 | 0.0862 | 75 | 0.1022 | 1049 | 383.6
VR2ACSR | Dove/VR2 | 1113 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 1.3905 |  |  |  | 25 | 0.0851 | 75 | 0.1009 | 1048 | 482
VR2ACSR | Eagle/VR2 | 1113 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 1.4295 |  |  |  | 25 | 0.0843 | 75 | 0.1 | 1051 | 690
VR2ACSR | Peacock/VR2 | 1210 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 1.4295 |  |  |  | 25 | 0.0792 | 75 | 0.0937 | 1140 | 417
VR2ACSR | Squab/VR2 | 1210 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 1.449 |  |  |  | 25 | 0.0787 | 75 | 0.0932 | 1140 | 524
VR2ACSR | Wood Duck/VR2 | 1210 | 30 | 7 | 0.142 | 0.142 | 0.426 | 1.491 |  |  |  | 25 | 0.0780 | 75 | 0.0923 | 1142 | 751
VR2ACSR | Teal/VR2 | 1210 | 30 | 19 | 0.0852 | 0.0852 | 0.426 | 1.491 |  |  |  | 25 | 0.0780 | 75 | 0.0924 | 1142 | 735
VR2ACSR | Swift/VR2 | 1272 | 36 | 1 | 0.1329 | 0.1329 | 0.1329 | 1.395 |  |  |  | 25 | 0.0768 | 75 | 0.0906 | 1192 | 94
VR2ACSR | Rook/VR2 | 1272 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.4655 |  |  |  | 25 | 0.0756 | 75 | 0.0894 | 1198 | 439
VR2ACSR | Grosbeak/VR2 | 1272 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 1.485 |  |  |  | 25 | 0.0752 | 75 | 0.0889 | 1198 | 551
VR2ACSR | Scoter/VR2 | 1272 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.5285 |  |  |  | 25 | 0.0745 | 75 | 0.0881 | 1201 | 789
VR2ACSR | Egret/VR2 | 1272 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.5285 |  |  |  | 25 | 0.0745 | 75 | 0.0881 | 1201 | 773
VR2ACSR | Flamingo/VR2 | 1333.2 | 24 | 7 | 0.1667 | 0.111 | 0.333 | 1.5 |  |  |  | 25 | 0.0724 | 75 | 0.0855 | 1256 | 495
VR2ACSR | Gannet/VR2 | 1333.2 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.521 |  |  |  | 25 | 0.0721 | 75 | 0.0850 | 1256 | 577
VR2ACSR | Stilt/VR2 | 1431 | 24 | 7 | 0.1727 | 0.1151 | 0.3453 | 1.554 |  |  |  | 25 | 0.0680 | 75 | 0.0801 | 1348 | 493
VR2ACSR | Starling/VR2 | 1431 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.5765 |  |  |  | 25 | 0.0675 | 75 | 0.0796 | 1348 | 620
VR2ACSR | Redwing/VR2 | 1431 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.6215 |  |  |  | 25 | 0.0669 | 75 | 0.0789 | 1351 | 869
VR2ACSR | Coot/VR2 | 1590 | 36 | 1 | 0.1486 | 0.1486 | 0.1486 | 1.56 |  |  |  | 25 | 0.0631 | 75 | 0.0739 | 1490 | 117
VR2ACSR | Tern/VR2 | 1590 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.5945 |  |  |  | 25 | 0.0627 | 75 | 0.0740 | 1498 | 292
VR2ACSR | Cuckoo/VR2 | 1590 | 24 | 7 | 0.182 | 0.1213 | 0.3639 | 1.63 |  |  |  | 25 | 0.0619 | 75 | 0.0727 | 1000 | 300
VR2ACSR | Condor/VR2 | 1590 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.63 |  |  |  | 25 | 0.0619 | 75 | 0.0745 | 1498 | 548
VR2ACSR | Drake/VR2 | 1590 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.662 |  |  |  | 25 | 0.0615 | 75 | 0.0723 | 1498 | 688
VR2ACSR | Mallard/VR2 | 1590 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.71 |  |  |  | 25 | 0.0609 | 75 | 0.0716 | 1501 | 966
VR2ACSR | Ruddy/VR2 | 1800 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.6965 |  |  |  | 25 | 0.0564 | 75 | 0.0662 | 1695 | 331
VR2ACSR | Canary/VR2 | 1800 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.743 |  |  |  | 25 | 0.0556 | 75 | 0.0666 | 1695 | 621
VR2ACSR | Rail/VR2 | 1908 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.7475 |  |  |  | 25 | 0.0537 | 75 | 0.0629 | 1797 | 351
VR2ACSR | Ortolan/VR2 | 2067 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.818 |  |  |  | 25 | 0.0503 | 75 | 0.5871 | 1947 | 380
VR2ACSR | Curlew/VR2 | 2067 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.8675 |  |  |  | 25 | 0.0496 | 75 | 0.0590 | 1947 | 712
VR2ACSR | Bluejay/VR2 | 2226 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.8885 |  |  |  | 25 | 0.0475 | 75 | 0.0552 | 2097 | 409
VR2ACSR | Finch/VR2 | 2226 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.9395 |  |  |  | 25 | 0.0469 | 75 | 0.0556 | 2107 | 751